## read me
General Explanation
The roombook resumes some requirements based on the preliminary safety report analyses and its update according to the modification on ITER plant (including PCR). This roombook is based on the references listed in this worksheet (see from line 29) and in the worksheet ``Version changes''. The areas and volumes for the rooms and the DS et FS Tag are under the Engage responsabilities. Some of this information remains TBD (To Be Defined).
The changes in this version (v2.10) are in red. This version of the roombook does not consider the PCR-466, as the new rooms in 14-L5 are not in the IO drawing <R> or in the Engage drawing <L> and the RFI 2062 is not complete. The PCR-628 is considered but it has no impact on the roombook.
The results presented in the roombook depends of openings in the vertical shafts . The figure below is based on the documents delivered in the frame of the FDR TB04 for B11 and B14 (see R7WEU2 v6.0: OME_DH_FD_110002_HV_v2.0 and OME_DH_FD_110005_HV_v2.0)
Main References
| Document title | reference IDM | Reference Roombook
| Preliminary Safety Report (RPrS) (3ZR2NC v3.0) | 3ZR2NC v3.0 | A
| Safety Important Functions and Components Classification Criteria and Methodology (347SF3 v1.8) | 347SF3 v1.8 | B
| Safety Requirements for ITER Facility Buildings | 2E4KSJ v3.9 | C
| Load Specifications for Buildings with Safety Requirements | 2ERTXQ v2.0 | D
| Load Specification Annex – Internal Explosions: Hydrogen Deflagration in Tokamak Complex | BMQ9XM v2.0 for KF63PB v2.1 to 2.7 BMQ9XM v3.0 for KF63PB v2.8 BMQ9XM v3.1 + SFK48R v1.0 for KF63PB v2.9 | E
| List Safety Defined Requirements (QDs) for Site & Buildings (PBS 61, 62, 63, 65) of ITER Nuclear Facility | FF92TR v2.0 | F
| Static and Transient Magnetic Field Maps in Tokamak Building | 3BQBVY v3.1 which in section 6 refers to the graphic maps available in QCTTFX v1.0 | G
| SL7 Meetings | 6XY3U3 v1.0 | H
| IO SL7 roombook | ITER_D_4ERMGZ v1.0 | I
| EDB for rooms tag | no IDM reference | J
| Engage drawings | ENG-_50_DW_111065_CW V2 ENG_40_DW_110373_FI V15 (MRR L4) | K L
| RFI-AE PA-941 - Follow-up to RFI-AE PA-817 - Pressure Relief Devices_ENG-06-RF-110107-NS_1 | RFI-AE PA-941 | M
| List Safety Defined Requirements (QDs) for Site & Buildings (PBS 61, 62, 63, 65) of ITER Nuclear Facility | FF92TR v2.0 | N
| Memo on 14-B1 Proposal to bring in line configuration of HVAC, DS, REMS | EGUK6P v2.0 | O
| Drawing for L3 | 28KXNH v2.8 | P
| Drawing for L4 | 28KYLN v2.8 | Q
| Drawing for L5 | 28KYM6 v2.8 | R
| Drawing for R1 | R3K8ZX v1.0 | S
| Drawing for B2 and B2M | 28KXJF v2.9 | T
| Drawing for B1 | 28JRZE v2.9 | U
| Drawing for L1 | 9QFFD3 v1.4 | V
| Drawing for L2 | 28KXMW v2.9 | X
| Engage Report on Roombook Data CW and FI Tokamak Complex (62-11, 62-14 and 62-74) FINISHING SCHEDULE | ENG-40-RG-110025-FI v09.0 (MRR L4) | Y
| B14 room data considered for PCR 412 | C8SALG v1.0 | Z
RFIs/SDRs/PCRs
| RFI-AE PA-941 - Follow-up to RFI-AE PA-817 - Pressure Relief Devices_ENG-06-RF-110107-NS_1 | RFI-AE PA-941
| RFI-AE PQ-2171 - hydrogen monitoring_OME-DD-RF-110053-NS_1 | SYMPC5
| RFI-AE PA-2196 - Nuclear Safety Room-Book KF63PB v2.8: Modes to be considered in case of accident in the DTR and NB Cell_ENERG-6200-IO-NSY-RF-009177-01_1 | T6V7LY
| RFI-AE PA-2197 - Nuclear Safety Room-Book KF63PB v2.8: Leak rate maximum to consider in normal conditions C2/C3_ENERG-6200-IO-NSY-RF-009178_1 | T6V8BV
| RFI-AE PA-2201 - Nuclear Safety Room-Book KF63PB v2.8: update of room list and changes on zonings_ENERG-6200-IO-NSY-RF-009180_1 | T73Q7J
| RFI-AE PA-2202 - Nuclear Safety Room-Book KF63PB v2.8: Design scenario to be considered for the PIC Cubicle rooms_ENERG-6212-IO-NSY-RF-009181_1 | T73QLD
| RFI-AE PA-2204 - Nuclear Safety Room-Book KF63PB v2.8: Fire protection_ENERG-6200-IO-NSY-RF-009183_1 | T74T79
| RFI-AE PA-2300 - Tokamak Complex - Temperature Requirements in case of Helium Leak in Galleries | TQDLN9
Notes
(1) | In the tritium building, the following situations are foreseen for the facility rooms for which there is no facing wall facing the confinement boundaries: • Internal fire: In the event of a fire in a facility room, no tritium release is foreseen in this room. Then, the considered conditions are fire event with overpressure (5000 Pa), temperature according to the eurocode, but without leak rate. • Overpressure 5000 Pa: In the event of a fire in a “process room” some tritium release could occurr but the fire is contained in the fire sector (process room). Then the considered condition in the adjacent facility room could be an.overpressure in the room (5000 Pa), with a specific leak rate, but without significant increase of temperature. For the latter case, the LR is 1 vol/day at 5000 Pa. There is no LR defined in 2E4KSJ <C> for the other buildings / rooms in case of fire
(2) | The LR is not applicable to the room but the confinement zone (or tritium plant fire sectors) - refer to 2E4KSJ <C>
(3) | Air-locks are connected to 2 areas. The LR of the both areas should be applied on the air-lock.
(4) | The requirements on leak rates are specified in the PCR412 outcomes
(5) | It is considered that no radioactive release can occur in the lift (i.e no radioactive materials transported or transported with safety transportation provision in order to exclude high radioactive inventories to be spread in this room).
(6) | This room has to be in under pressure compared to the atmospheric pressure, and the exhaust flow shall be sent to the chimney.
(7) | PIC/SIC-1 cubicles shall include an automatic fire detection and suppression system. Alarm shall be reported to the control rooms (normal and back-up control room).
All the cubicles (PIC/SIC-2, non PIC, SR) located in the same room with at least one non-redundant cubicle PIC/SIC-2 shall be equipped with an automatic fire detection and suppression system. The redundant PIC/SIC-2 cubicles, can be implemented with the SR, and non-PIC cubicles and, in this case, this room (and not the cubicles themselves) is equipped with automatic fire detection and suppression systems. Alarm shall be reported to the control rooms (normal and back-up control room). The minimum distance between PIC/SIC-2 cubicles and non PIC cubicles is 2m.
(8) | This represents the worst local atmsophere temperature (air temperature), depending on where and how big is the leak. But the global atmosphere and surface temperature is much higher As clarified by RFI 2300, the temperature of equipment surface (meaning concrete walls extrapolated to the equipment) to be considered is 11 degC, but the temperature inside the HVAC ducts will be comprised between -170 and 11 degC, depending on the duct location compared to the cryoline break according to <D>.
(9) | The localisation of manual extinction has to be defined. It is not required to have an extinguisher in each room, but extinguishers shall be set up taking into account that the Tokamak buidling is not accessible in mode 0 and 2.
(10) | 2 levels of filtration are required for VVPSS room. However, it is not required to ventilate this room by C3 network
(11) | 11-R1-02 shall be fitted with automatic fire suppression systems. It is not required that this system covers all the room. Localised systems could be implemented instead of a global system, if required (based on fire risk analysis to be perforemd by the contractor)
(12) | All provisions shall be implemented to avoid to go through the last confinement boundary. Where there is an opening, isolations devices shall be implemented to ensure that the leak rate of the confinement boundary is guaranteed and to avoid contamination propagation outside this confinement boundary
(13) | The boundary limits (where the confinement / leak rates applies) is up to the designers possibilities, provided that a global leak rate applies for these "external walls" boundary (last confinement boundary)
(14) | However, the walls which are part of the confinement boundary have to ensure the leak-rate required. The leak-rate of the potential openings on the last confinement walls have also to comply with the global leak rate. The LR may not be applicable to the room itself but sometimes only to the walls of the 6 faces (walls, floor, ceiling) adjacent to DS sectors or fire sectors; then confinement requirements should nevertheless be applied for those walls - refer to 2E4KSJ <C>
(15) | The doses at the end of life mentioned in the current roombook should not be taken into account anymore. The doses at the end of life in normal situation, room by room, should be provided by the NIU (Nuclear Integration Unit) from its radiation map and should take into account uncertainties. The doses at the end of life in accidental situation will then be defined by IO/SD. The original values have been kept only for memory.
(16) | PIC/SIC-2 : redundancy requirement including utilities (electrical power, I&C, …)
(17) | The fixed part of the manual extinction shall be operable and PIC/SIC-2
(18) | For the confinement zone ``14-Facility rooms_by levels'': - in accordance with the RFI 1777, the leak tightness requirement applies on the last confinement boundary. Therefore the qualified leak rate applies to the overall confinement zone “facility room by level” without specific requirement between 2 levels of the zone, - in accordance with a defined requirement associated to the PCR 412, isolation valves must be implemented on HVAC ducts at B2 and L1 levels, preventing radioactive products transfer through HVAC network to another level.
(19) | As stated in the RFI 1744, for a DS sector ``2+2 but mutualization possible’’ means that this DS sector must be fitted with at least 1 isolation damper that is exclusively dedicated to it and that the other isolation damper may be shared among some DS sectors.
(20) | For the rooms whose the confinement zone for accidental events is the 1114-Vault or the 11-DTR or the 11-NB Cell: - Each room containing combustible liquids (i.e. oil lubrification for pump) shall be fitted with an automatic PIC/SIC-1 fire detection and suppression system located above the locations where the combustible liquids are present. The fire suppression shall generate only a low volume of effluent.
(21) | There shall not be any common mode failure between the safety chiller units located at 11-R1-01E and at 14-R1-03, neither by fire, nor by any external event.
(22) | For rooms 11-R1-A1/03/04A/04B, they are not in the IO baseline drawings (<S> for level R1), but they appear in Engage documents. Such modification shall have been included via a deviation request and a PCR. The data associated with these rooms are therefore not validated. For rooms 14-R1-02, 14-R2-L1, 14-R2-S1, following RFI 2201, they do not exist in Engage drawings nor in IO baseline drawings.
(23) | These rooms are in this roombook as they are in the Engage drawing <L>. However they are not in the IO baseline drawings. Their requirements will be defined when the design is detailed. Deviation request and PCR need to be submitted for such modification.
(24) | Specific shielding for the room according to PCR-487
(25) | Following RFI 2201: 1 rooms is requested to be added: 11-L5-LFT. 3 rooms are requested to be deleted: 11-R1-01E, 11-R1-01W, 14-L1-F3. Deviation request and PCR should be submitted for such modifiation comparing to IO baseline drawing.
(26) | The FS tags in Engage document have some incoherences (<L> and <Y> ). FS tages in Engage drawing <L> are used in this case.
(27) | The room surfaces and room volumes are taken from the Engage document <Y> . The change of room surfaces and room volumes in future versions (except the addition for which is was written TBD) should be validated by deviation request and PCR process because the change of room volume/surface could challenge the safety analysis. The room volumes used as input data of safety analysis used for PCR412 are given in <Z> for information (but it has been checked that the current volume in this roombook does not challenge the results of PCR 412).
(28) | PIC cubicle rooms are located in zones which could be impacted by accidents that occur from other rooms (LOCA, helium leak, hydrogen deflagration, etc) or external hazards. a) The structure (civil work, doors, etc) should be designed to withstand such conditions b) Buidling systems that penetrate the PIC cubicle room walls (HVAC ducts, pipes) should be designed to be able to prevent the entry of accdiental condition from the adjacent rooms into the PIC cubicle rooms. c) Systems and components located inside the PIC cubicle rooms should be designed to maintain their functions under environmental conditions depending on the design of the buidling systems as identified in above point b). The PIC cubicles should thus be prevented from being lost by accidents or external hazards.
(29) | The reference <G> takes precedence to the values of the roombook that are here only for convenience, as the values of <G> shall be read in a 3D mode
Legend for liquid confinement
(*) | no leak tightness criteria, just the adequate construction quality
(**) | yes for water tightness but only up to the flooding volume (depending on the retention volume), no water leak rate criteria, just the adequate construction quality
(***) | yes for water tightness but only up to the flooding volume (depending on the retention volume), water leak rate criteria = no leak admissible
Liner height : | the floor liner height shall not be zero, it shall be the height of the retention volume due to flooding risks
Legend for airplane crash
yes | The room has to be protected against direct and indirect effect of air plane crash
no | the room is already protected by the overall building resistance insured by external walls (against direct and indirect effects)
no* | The room is not protected but the direct or indirect impact of the air plane crash shall not affect a PIC equipment or building
Minimal section of ventilation exhaust duct
The maximum air speed in ventilation is 10 m/s, to have a sufficient exhaust ventilation duct section in Fire sectors. Therefore a minimal duct section has to be guaranteed
Waste zoning
ZDC: | conventional (non-radioactive) waste
ZDN: | nuclear (radioactive) waste
Ventilation zoning
XX-HVAC or XX | Ventilation ensured by HVAC system
XX-DS | Ventilation ensured by the Detritiation System
XX-HVAC/DS | Ventilation ensured by the HVAC system or DS system, depending on the situation
C3/HVAC/DS fix or mobile | During specific operations, a mobile HVAC system could be used
Radiological zoning
white | unregulated zone (< 80 μSv in one month)
Blue | supervised zone (< 7.5 μSv in one hour )
Green | controlled zone - not specially regulated (< 10 μSv/h)
Yellow | controlled zone - specially regulated (< 100 μSv/h) see assumption below
Orange | controlled zone - specially regulated (< 100 mSv/h)
Red | controlled zone - human access forbidden without special authorization (≥ 100 mSv/h)
Note: the limits of the dose rate for ITER facilities are lower than the regulatory values (25 µSv/h for green zone and 2mSv/h for yellow zone according to French order of 15/05/06).
Anti-deflagration zoning
No zone | no hazard present, so no zone required
zone 0 | location where an explosive atmosphere consisting of a mixture of air and inflammable gases, vapours or mist is present permanently, frequently or during long periods
zone 1 | location where an explosive atmosphere consisting of a mixture of air and inflammable gases, vapours or mist is liable to be present occasionally under normal operation
zone 2 | location where an explosive atmosphere consisting of a mixture of air and inflammable gases, vapours or mist is not likely to be present under normal operations or, if present, only for short periods.
zone 20 | location where explosive atmosphere in the form of combustible dust cloud is present in the air permanently, frequently or during long periods.
zone 21 | location where explosive atmosphere in the form of combustible dust cloud is liable to be present occasionally under normal operation.
zone 22 | location where explosive atmosphere in the form of combustible dust cloud is not likely to be present under normal operation or, if present, only for a short period.
no zone except zone 2 with 1,5 m around specific capacities | no zone except zone 2 with 1,5 m around specific capacities
Beryllium zoning
no Be | no Beryllium
NCZ (Be) | Beryllium no controlled zone
CZ (Be) | Beryllium controlled zone
BCZ (Be) | Beryllium zone with respiratory protection

## version changes
Intial version V1.1 the 12th september 2013
Changes in version V2.1 the 2nd February 2015
The main modifications are described in the table below :
| Modification subject | Type of modification | Sources
| Room list | Updated according to EDB version and PCR 412 on going | EDB January 2015 <J> and data sent by Engage on PCR412
| Room tag | Updated according to EDB version | EDB January 2015 <J> and data sent by Engage on PCR412
| Volume/Surface | Data sent by email by Engage the 19/11/2014 | Engage mail
| Resistance air plane crash | Updated according to data provided by Engage | PCR 390 ENG-_50_DW_111065_CW V1 <K>
| Internal fire | Correction on some fire damper PIC class
| Overpressure | correction to include the boundaries of the last confinement barrier | Engage drawing : ENG_40_DW_110373_FI V11 <L>
| C1-Cr LOVA III | Correction to ensure consistency : accident added in airlock of B11
| X8- Loss of coolant in Port cell | Correction to ensure consistency : accident added in airlock of the B11
| Helium leak in galleries | Helium in port cell deleted in vault and port cell | Consistency with 2ERTXQ <D>
Accident added in PIC room of Tokamak to be compliant with other risk
Correction to ensure consistency : accident added in airlock of B11
| Explosion in B14 | Consequences added in the vault | PCR 412 and BMQ9XM <E>
| DTR LOCA III | Correction : consequences of propagation in the vault added
| Leak to galleries | Correction to ensure consistency : accident added in airlock of B11
| NB cell internal explosion | Consistencies of values between NB cell and NB cell airlock Temperature modification according to RFI and 2ERTXQ | RFI 1434 and 2ERTXQ <D>
| Dynamic confinement of tritium | Nota (13)added | Engage drawing : ENG_40_DW_110373_FI V11 <L>
Correction PIC class modified for 14 L3 A1 and 14 L3 A3
Correction to include the boundaries of the last confinement barrier
Correction for consistency 2-2 mutualisation possible for PNW and PSW isolation valves
| Fire extinction | Modification into automatic fire suppression system to be compliant with the QD | FF92TR <F>
|  | Fire suppression system for fuelling line deleted in L1 | RFI-AE PA-1317 RFI-AE PA-1656
|  | Fire extinction in the vault | PCR 412
|  | Consistency SIC 2 replaced by SIC 1 for automatic fire extinction system | FF92TR <F> version that includes last version PCR 412 QD with discharge in the vault
FF92TR <F> requirement compliance
| Fire sectorisation | Correction insulated cables for 14 B2 25
|  | Fire sectorisation tag modified | Consistency with CMM : Engage modification (Engage is responsible for the tagging)
| Ventilation zoning | C3 DS corrected for B1 drain tank room
| End life dose | Correction end life dose added to rooms near the tokamak wall
Correction dose in VPS room
| Magnetic zoning | Data missing in first version : Data added in tritium plant and diagnostic building | 3BQBVY <G>
| Waste zoning | Correction error on previous version
11 L1-23 : ZDC to ZDN
11 R1 03 : ZDN to ZDC
| Beryllium zoning | Correction error on previous version 11 L1 23
| Lightning zoning | Some typo correction into LPZ1
Changes in version V2.2 the 3rd March 2015
The main modifications are described in the table below (comments from reviewers) :
| Modification subject | Type of modification | Sources
| Room list | Correction inconsistency on 14-L2- L1 and L2 | EDB January 2015 <J>
| Confinement zone for accidental events | PIC room in the TKM : PIC rooms replaced by galleries
| Watertight | Consistency for B2 level requirements Levelling layer replaced by slope Modification on shaft, wall characteristics added to be consistent Some correction on port cell and airlock
| Various | Nota added to give explanation Version changes added Documents in reference SIC replaced by PIC Correction nota (20) replace by (13) Correction some nota (9) replaced by (7)
Changes in version V2.3 the 4th March 2015
| Modification subject | Type of modification | Sources
| Watertight | Consistency for B2 level requirements Levelling layer replaced by slope
| Various | Version changes added Documents in reference Typo corrected
Changes in version V2.4
| Modification subject | Type of modification | Sources
| Watertight | Consistency for B2 level requirements (***) Levelling layer replaced by slope in forgotten lines
| type of fire extinction in 14-B2M/B1/L1/L2/L3-V4 | Deletion of process extinction, the needs is to have a SIC1-1 (redundant) fire extinction in the room
| Classification PIC/SIC for isolation dampers, fire dampers, fire detection, fire extinction | Consistency with defined requirement | Appendix C of FF92TR document <N>
| Various | Version changes added Documents in reference Typo corrected Nota (15) and (16) added Consistency room designation with EBD
Changes in version V2.5
| Modification subject | Type of modification | Sources
| Classification PIC/SIC for fire extinction | Consistency with defined requirement | FF92TR document <N>
| Various | Nota (17) added and (9) modified
Changes in version V2.6
| Modification subject | Type of modification | Sources
| Various | Editorial modification
Changes in version V2.6
| Modification subject | Type of modification | Sources
| Dynamic containement tritium for 14-B1-22 and 14-B1-22A | Correction | PCR412 <0>
Changes in version V2.8
| Modification subject | Type of modification | Sources
| Room list | Addition of the rooms 11-R1-01W, 14-L3-A5, 14-L3-F1, 14-L4-A5, 14-L5-A5, 74-L4-29 and 74-L5-03 Change in the tags of the rooms 14-L4-A5, A6 and A7 | Drawings <P> to <S>
|  | Addition of the room 11-R1-A1 but with nota (22) | RFI 1659
|  | Addition of the nota (22) for the rooms 11-R1-03, 11-R1-04A and 11-R1-04B | <S>
|  | Addition of the rooms 14-R1-02, 14-R2-L1 and 14-R2-S1 but with nota (22) | <J>
| Fire break zones | Changes in confinement zones for accidental events, leak rate in case of fire, leak rate in case of overpressure 5 kPa, leak rate at 300 Pa, DS zone tag
| 14-R1-A1 | Changes for water tightness
| Confinement zone for accidental events | Change for rooms 11-R1-04A and B | RFI 1672
|  | Nota (18) | RFI 1777 and QETVTS v3.0
| Water tightness | Modification for 11-R1-01E, 11-R1-01W, 14-R1-01 and 14-R1-03
| Leak-rate at 300 Pa | Change for 14-(B2 and L1 to L5)-A5
| Hydrogen deflagration in the Tritium Building | New values | <E>
| C1-Cr LOVA III - Cryostat Air Ingress (1 m² break) | Change for 14-L3-22 and 14-L3-A2
| X8 - Loss of coolant in Port Cell - (LOCA III) | Change for 14-L4-L2
| External overpressure resistance of PIC cubicle rooms | New values in B14 | <E>
| Dynamic confinement of Tritium | Nota (19) | RFI 1744
Change for 14-L1-F3
| Type of fire extinction | Change for the following rooms of B14: B1-27, B1-28, B2-22, B2-24, B2-25, B2M-01 and L1-24, | RFI 1678
| Radiological zoning | Zone red for all the rooms at R1 or R2 level of B11 and B14 in mode 0
Change of zoning for some rooms at R1 or R2 level of B11 and B14 in modes 1 and 2
Correction of the filled colours (so that they are consistent with the zoning)
| Anti-deflagration zoning | Change for the rooms 11-B2-02E, 11-B2-02W and 11-L5-ASW | RFI 1687
| Read me | Change in the figure related to the openings of the vertical shafts lines 10 to 25 | See line 8 before the figure
Nota (4)
|  | Nota (20) | QETVTS v3.0
Nota (21)
|  | Nota (22) | See this Nota
Changes in version V2.9
| Modification subject | Type of modification | Sources
| Room list | Addition of the rooms 14-(L2 and L3)-V6 | Drawing <L> and RFI 1966. The room 14-L4-24 mentioned in the RFI is not added as it is not in <L>
| Room description | Correction for 14-L5-TG1 and 14-L5-TG2 | Drawing <R>
| Resistance against aircraft crash | Correction for 14-L4-29 | Drawing ENG-50-DW-111065-CW-v2.0
| Hydrogen deflagration in the Tritium Building | New values | <E>
| V3-LOVA III - Loss of vacuum through on VV / cryostat penetration line | Correction of a typo for the values of ∆P min (kPa) : -24000 -> -24
| DS zone tag | Correction for 14-B2-25 | RFI 2026
|  | Correction for 11-L3-04NE | RFI 2055
| FS tag | Changes for 14-B1-23, 14-L1-F1, 14-L3-F1, 14-L3-A5, 14-L4-A5, 14-L4-(20 to 23) | Drawing <L>
| Fire protection/PIC level of detection | Correction for 19-B2-01 | QETVTS v3.0 (QD0419)
| Fire protection/PIC level of fire extinction | Change for 11-B1-01 and 11-B2-01
| Ventilation zoning | Correction for 11-B1-01 and 11-B2-01
| HEPA | Correction for 14-B2-22
Correction for 74-L4-29
| Read me | Line 36: Update of the reference for the Static and Transient Magnetic Field Maps. It does not lead to a change in the dedicated column of the roombook
Line 40: Update of the references for the airplane crash zoning and the fire zoning. It does not lead to a change in the column of the roombook dedicated to airplane crash.
Nota (15), (23) and (24)
Changes in version V2.10
| Modification subject | Type of modification | Sources
| Room list | 1. Following RFI 2201, 3 rooms 14-R1-02, 14-R2-L1, 14-R2-S1 are removed. They don't exist in IO baseline drawing <S> nor in Engage drawing <L>. 2. Other requests of adding/removing rooms from RFI 2201 are not considered. - Regarding the two rooms in B14 L5 following PCR 466 (14-L5-03A/14-L5-05B), PCR approval and IO baseline drawing update should be prior to the roombook update. - regarding other requests for rooms: a deviation request and a PCR should be added before adding or removing rooms in the roombook, see also nota 22, 23, 25. | RFI 2201
| Room tag | B14 technical galleries are located in mezzanine. Their room tags are updated (from 14-xx-TGx to 14-xxM-TGx): -14-B2M/B1M/L1M/L2M/L3M/L4M/L5M-TG1 and 14-B2M/B1M/L1M/L2M/L3M/L4M/L5M-TG2 To be noted that the mezzanines (TG) are not detailed in IO baseline drawings (<P> to <X>). They have been specified in the roombook to avoid confusion with rooms located just below the technical galleries in the same level. | <L> <Y>
| Room description | The room description for 11-L4-04/11-L3-02E following PCR 662 which changes the layout of TCWS.
| Room area and room volume | New values are taken from Engage drawing <L> and finishing schedule <Y>. The versions approved during MRR L4 are used. A nota (27) is added for the change of room volumes/surfaces. | <L> <Y> <Z>
| Confinement zone for accidental events | Following RFI 2201: - The fire break zone in B14 (14-xx-Fx) belong to air locks -Confinement zone name of the SIC-2 cubicle rooms in B11 are "11-SIC cubicle rooms": 11-B2-05NE, 11-B2-05NW, 11-B2-05SE, 11-L1-05NW, 11-L2-05SE. - PIC has replaced SIC for PIC cubicles rooms | RFI 2201
| Water tightness | 74-B2-12 floor is changed from Yes (**) to Yes (*). 74-B2-ANW and 74-B2-ASW requirement are changed to Yes (***) for walls and floors.
| Liner Type (Floor) | Liner type in B74 is changed following RFI 2201: - Decontamination is not required for staircases, corridors in B74: 74-B2-10/SN1/SS1, 74-B1-14/LFT/SN1/SS1, 74-L1-13/23/LS1/SN1/SS1, 74-L2-24/27/LS1/SN1/SS1, 74-L3-04/09/LS1/SN1/SS1, 74-L4-29/LS1/SN1/SS1, 74-L5-02/03/LS1/SN1/SS1. | RFI 2201
| Confinement for Normal conditions C2/C3 | Following RFI 2197: - Several rooms are not inside the DS-sector zone, no specific leak rate is required for the walls not in contact with a DS-sector zone: 14-L2-05A, 14-L3-05A, 74-L4-29, 74-L5-03. - 14-B2M-V4 and 14-L3-F1 leak rate requirement should be the leak rate for the process rooms. They are changed to 1 (FS). - 14-B2M-02 leak rate requirement is the same as for external wall. | RFI 2197
| Hydrogen deflagration effects from the Tritium Building | Title of the column is changed into Hydrogen deflagration effects from the Tritium Building
| ∆P (Pa) in case of X5 - LOCA IV - Large DV ex-vessel coolant pipe break | 11-L3-04NE - SIC-1 cubicle room is located in vault area. These accidents will concern this room as the other vault area. The accidental conditions following these accidents are also updated for 11-L3-04NE. On the other way, the conditions applied for the gallery are not concerned by 11-L3-04NE any more. Leak to galleries (LOCA III) / Leakage from Port Cell/Vault/NB cell in case of LOCA and HLG - Helium Leak in Gallery will not concern 11-L3-04NE. | RFI 2202
X8 - Loss of coolant in Port Cell - (LOCA III)
DTR LOCA III - Large VV ex-vessel coolant pipe break in DTR
NB Cell internal Explosion Hydrogen-dust explosion in Vacuum Vessel
| DTR LOCA III - Large VV ex-vessel coolant pipe break in DTR / Mode | A LOCA is always possible in mode 0 and at the beginning of mode 1 when cooling water conditions are still hot. But it is assumed that workers, for whom HVAC actuation will be needed prior to their entrance, will enter only when the risks are reduced. Therefore, HVAC is isolated at the beginning of mode 1 and will not have to be designed (except the isolation valves protecting it) against LOCA in such mode 1. | RFI 2196 RFI 1455
| NB Cell internal Explosion Hydrogen-dust explosion in Vacuum Vessel / Mode | Explosion in NB cell (from VV or NB explosion) can occur in all modes, for which there are always hydrogen and dust. But it is assumed that workers, for whom HVAC actuation will be needed prior to their entrance, will enter only in mode 1 when the risks are reduced. Therefore, HVAC is isolated in the modes for which workers are not present and actuated only when risks are reduced to allow worker's entrance. Therefore HVAC will not have to be designed for the mode 1 and will not have to be designed (except the isolation valves protecting it) against LOCA in such mode 1. The request in RFI 2196 about the NB cell airlock is not accepted. The NB cell airlock is concerned by this accident. | RFI 2196 RFI 1455
| Hydrogen monitoring in the room | Rooms with requirement of hydrogent monitoring are identified in the roombook following RFI 2171. The room 14-L1-L1 has been excluded from the list as there is no hydrogen risk in this room. (after checking with RFI answer author). | RFI 2171
| External overpressure resistance of PIC cubicle rooms | Following RFI 2202, a nota 28 is added to clarify the accidental conditions for PIC cubicle rooms in case of accidents. The cargo lift PIC cubicle rooms 11-R1-04A and 11-R1-04B do not exist in IO baseline drawing (<S>). A deviation request and a PCR should be submitted for such modification (see nota 22). The design data of the room are not finalized and are not considered. | TVRFNK v1.0 (section 5.1) RFI 2202
| Fire Cables trays protection | The cable tray fire protection for 14-XX-A5 is insulated material. The rooms 14- B2/B1/L1/L2-A5 are modified.
| FS tag | FS tag updated with Engage drawing <L> and finishing schedule <Y>. The versions approved during MRR L4 are used. When there is an inconsistence between Engage drawing and finishing schedule, the FS tag from Engage drawing is used, see nota 26. | <L> <Y>
| PIC level of detection | Following RFI 2204, the fire detection is upgraded to PIC/SIC-1 for rooms with PIC/SIC-1 fire dampers. | RFI 2204
| Ventilation zoning | Ventilation zoning is updated for 11-L3-04NE for mode 0, 1, 2. | RFI 2201
In mode 1, the C3 HVAC is replaced by C3 HVAC/DS for clarification.
The Min air change rate is corrected for rooms 11-B1-01, 11-B2-01, 11-L3-04NE.
| HEPA filters | The number of filteration level is updated for 11-L3-04NE. | RFI 2201
| Magnetic zoning | The magenitic field value in 11-L2-LFT is corrected. A nota 29 is added. | <G>
| Read me | Line 36: Engage fire zoning drawing version is updated. The referred version is validated in MRR L4.
Line 52: Engage finishing schedule is added for new values of room surface and volume.
Line 53: PCR 412 report is added to verify the new room volumes in B14.
RFIs are added which introduced modification of the room book in v2.10.
nota (8) (14) (15) are revised to add precisions.
nota (20) is revised to remove redundant information already given in nota (7).
nota (22), (23) are revised
5 new nota (25), (26), (27), (28), (29) are added.

## NS Room Book
[8 empty] | Liquid confinement |  |  |  | Confinement of releases of fire | [8 empty] | Confinement normal & accidental events |  |  |  |  | 13.2 | 13.2 | [46 empty] | Hydrogen Monitoring |  | Resistance external overpressure |  |  |  | Requirement of dynamic confinement of Tritium releases |  |  |  | Fire mitigation | [7 empty] | Ventilation zoning | [7 empty] | HEPA filters |  |  | Radiological conditions | [5 empty] | Miscellaneous conditions
12
[7 empty] | Resistance against aircraft crash see read me |  | Water tightness (see read me) |  |  |  | Internal Fire event |  |  |  |  | Overpressure 5 kPa (1) |  |  |  | Normal conditions C2/C3 (RFI 2197) | Hydrogen deflagration effects from the Tritium Building (4) |  | C1-Cr LOVA III - Cryostat Air Ingress (1 m² break) | [6 empty] | X5 - LOCA IV - Large DV ex-vessel coolant pipe break |  |  |  |  | NB Cell LOCA III (X8 bis) - LOCA design scenario in NB cell (LOCA III) |  |  |  |  | X8 - Loss of coolant in Port Cell - (LOCA III) |  |  |  |  | HLG - Helium Leak in Gallery / Cryogenic leak in Galleries |  |  |  |  | V3-LOVA III - Loss of vacuum through on VV / cryostat penetration line | [6 empty] | DTR LOCA III - Large VV ex-vessel coolant pipe break in DTR |  |  |  |  | Leak to galleries (LOCA III) / Leakage from Port Cell/Vault/NB cell in case of LOCA |  |  |  |  | NB Cell internal Explosion Hydrogen-dust explosion in Vacuum Vessel | [5 empty] | Hydrogen monitoring in the room |  | External overpressure resistance of PIC cubicle rooms |  |  |  | Dynamic confinement of Tritium |  |  |  | Fire sectorisation | [7 empty] | Ventilation zoning | [7 empty] | HEPA |  |  | Radiological zoning |  |  | Dose at the end of the life (Gy) (15) |  |  | Magnetic zoning (nota 29) | Miscellaneous zoning |  |  | Lightning zone
Bldg | Room Tag | Room description | Room area in ENG-40-RG-110025-FI-09.0 (nota 27) | Room volume in ENG-40-RG-110025-FI-09.0 (nota 27) | Free volume taken in safety analysis [m³] | Confinement zone for accidental events (18) (RFI 2201) |  |  | Floor | Walls | Liner Type (Floor) |  | Applicable Y/N | ∆P (Pa) | T (0C) | Leak rate max (vol/day) at +-5000 kPa | Modes | Applicable Y/N | Leak rate max (vol/day) (2) | Modes |  | Leak rate max at 300 Pa (vol/day) (2) | Applicable Y/N | Max pressure (bar abs) (see BMQ9XM) | Applicable Y/N | ∆P (Pa) | ∆P Max (Pa) | T min (0C) | T Max (0C) | Leak rate max (vol/day) (2) | Modes | Applicable Y/N | ∆P (Pa) (RFI 2202) | T (0C) | Leak rate max (vol/day) (2) | Modes | Applicable Y/N | ∆P (Pa) | T (0C) | Leak rate max (vol/day) | Modes | Applicable Y/N | ∆P (Pa) | T (0C) | Leak rate max (vol/day) | Modes | Applicable Y/N | ∆P (Pa) | T (0C) | Leak rate max (vol/day) (2) | Modes | Applicable Y/N | ∆P min (kPa) | ∆P Max (kPa) | T Min (0C) | T Max (0C) | Leak rate max (vol/day) (2) | Modes | Applicable Y/N | ∆P (Pa) | T (0C) | Leak rate max (vol/day) (2) | Modes (RFI 2196/1455) | Applicable Y/N | ∆P (Pa) | T (0C) | Leak rate max (vol/day) (2) | Modes | Applicable Y/N | ∆P (Pa) | T (0C) | Leak rate max (vol/day) (2) | Modes (RFI 2196/1455) |  | RFI 2171 |  | Applicable Y/N | ∆P (kPa) Nota 28 | Modes |  | DS zone Tag | Number (inlet + outlet) (19) | PIC class |  | Fire Cables trays protection | FS tag | PIC level of fire dampers | REI | PIC level of detection (20) RFI 2204 | Type of fire extinction (7) (20) | PIC level of fire extinction (20) |  | Mode 0 | Min Air Change rate 0 (in vol/h) | Mode 1 | Min Air Change rate 1 (in vol/h) | Mode 2 | Min Air Change rate 2 (in vol/h) | DS or HVAC minimal exhaust duct surface (see read me) |  | PIC Class | Filtration level on exhaust |  | Mode 0 | Mode 1 | Mode 2 | Normal situation | Acc. Situation |  | Mode 0 | Waste zoning | Anti-deflagration zoning | Be zoning
11 | 11-B1-01 | TCWS Drain Tanks Upper Level | 75.39 | 1834.833 | 1174.293 | 11-Drain tank Room | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 300 or 100 000 (300 if no air pathway following a LOCA in the vault (design dependant), 100 000 if air pathway) | 130 if air pathway from the vault (design dependant), NA if not | 1 if air pathway to the vault; 0.055 else (design dependant) | 0 | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | Yes | 100000 | 125 | 1 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 0 or 20000 (0 if no air pathway, 20 000 if air pathway) | 100 |  | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-01 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-01 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C3-DS | 1 | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 460.8297 | 623.8297 |  | 6 mT B≤ 18 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | NA (no Be) | LPZ 1
11 | 11-B1-02E | Divertor Gallery E | 737.7472 | 3198.949 | 2367.222 | 11-Gallery area | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-05 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-02 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | automatic fire suppression system for fuelling lines | PIC/SIC-1 |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 174298.2815 | 174298.2815 |  | 5 mT B≤ 37 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-02N | Divertor Gallery N | 493.6228 | 2111.094 | 1562.209 | 11-Gallery area | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-05 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-02 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 174298.1724 | 174298.1724 |  | 15 mT B≤ 37 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-B1-02S | Divertor Gallery S | 622.1904 | 2706.211 | 2002.596 | 11-Gallery area | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-05 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-02 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 174298.2815 | 174298.2815 |  | 15 mT B≤ 37 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-B1-02W | Divertor Gallery W | 702.8915 | 3049.651 | 2256.742 | 11-Gallery area | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-05 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-02 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 174298.2815 | 174298.2815 |  | 5 mT B≤ 37 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-B1-C01 | Port Cell C01 | 56.5324 | 259.9867 | 246.9874 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-41 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-14 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 407657.9009 | 407657.9009 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-C02 | Port Cell C02 | 48.8905 | 224.2399 | 213.0279 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-42 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-13 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 706857.8987 | 706857.8987 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-C03 | Port Cell C03 | 57.0381 | 262.3899 | 249.2704 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-43 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-12 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 407657.8978 | 407657.8978 |  | 49 mT B≤ 248 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-B1-C04 | Port Cell C04 | 57.0367 | 253.545 | 240.8678 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-44 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-11 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 407657.8978 | 407657.8978 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-C05 | Port Cell C05 | 57.2621 | 254.4084 | 241.6879 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-45 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-10 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 407657.8978 | 407657.8978 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-C06 | Port Cell C06 | 57.0379 | 253.55 | 240.8725 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-46 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-27 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 407657.8978 | 407657.8978 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-C07 | Port Cell C07 | 65.184 | 292.2436 | 277.6314 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-47 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-26 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 407657.8978 | 407657.8978 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-C08 | Port Cell C08 | 48.8796 | 224.1781 | 212.9692 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-48 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-25 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 412902.299 | 412902.299 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-C09 | Port Cell C09 | 57.0638 | 262.5068 | 249.3815 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-49 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-24 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 407657.8978 | 407657.8978 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-C10 | Port Cell C10 | 55.0535 | 252.9592 | 240.3113 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-50 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-23 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 407657.8978 | 407657.8978 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-C11 | Port Cell C11 | 57.0407 | 262.4028 | 249.2827 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-51 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-22 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 407657.8978 | 407657.8978 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-C12 | Port Cell C12 | 57.0381 | 262.3904 | 249.2709 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-52 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-21 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 407657.8978 | 407657.8978 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-C13 | Port Cell C13 | 65.184 | 301.0834 | 286.0292 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-53 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-20 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 407657.8978 | 407657.8978 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-C14 | Port Cell C14 | 49.0922 | 225.0336 | 213.7819 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-54 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-19 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 412902.299 | 412902.299 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-C15 | Port Cell C15 | 57.0381 | 262.3904 | 249.2708 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-55 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-18 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 407657.8978 | 407657.8978 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-C16 | Port Cell C16 | 57.0381 | 262.3904 | 249.2708 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-56 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-17 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 407657.8978 | 407657.8978 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-C17 | Port Cell C17 | 57.0381 | 262.3904 | 249.2708 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-57 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-16 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 407657.8978 | 407657.8978 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-C18 | Port Cell C18 | 62.983 | 290.6162 | 276.0854 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 5 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-58 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-15 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 407657.8978 | 407657.8978 |  | 49 mT B≤ 248 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-B1-LFT | Tokamak Cargo Lift | TBD | 413.6866 | 393 | 11-Cargo-lift area | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (insulated) | 11-FS-07 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 328.1032 | 328.1032 |  | 6 mT B≤ 18 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-B1-PNW | NW Cryo-line Shaft | TBD | 48.1074 | 46 | 11-Gallery area | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-59 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 3093.112 | 3093.112 |  | 5 mT B≤ 6 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-B1-PSW | SW Cryo-Line Shaft | TBD | 42.8995 | 41 | 11-Gallery area | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-63 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 31.042 | 31.042 |  | 7 mT B≤ 10 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-V01 | Vertical Shaft V01 | TBD | 33.7174 | 32 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 584200.5922 | 584200.5922 |  | 55 mT B≤ 73 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | NA (no Be) | LPZ 1
11 | 11-B1-V02 | Vertical Shaft V02 | TBD | 30.5813 | 29 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 584205.8366 | 584205.8366 |  | 55 mT B≤ 73 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-V03 | Vertical Shaft V03 | TBD | 39.4259 | 37 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 584200.5922 | 584200.5922 |  | 55 mT B≤ 73 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | NA (no Be) | LPZ 1
11 | 11-B1-V04 | Vertical Shaft V04 | TBD | 35.6711 | 34 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 584200.5922 | 584200.5922 |  | 55 mT B≤ 73 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-V05 | Vertical Shaft V05 | TBD | 35.671 | 34 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 584200.5922 | 584200.5922 |  | 55 mT B≤ 73 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-V06 | Vertical Shaft V06 | TBD | 35.671 | 34 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 584200.5922 | 584200.5922 |  | 55 mT B≤ 73 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-V07 | Vertical Shaft V07 | TBD | 35.671 | 34 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 584200.5922 | 584200.5922 |  | 55 mT B≤ 73 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-V08 | Vertical Shaft V08 | TBD | 35.671 | 34 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 584205.8366 | 584205.8366 |  | 55 mT B≤ 73 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-V09 | Vertical Shaft V09 | TBD | 39.4259 | 37 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 584200.5922 | 584200.5922 |  | 55 mT B≤ 73 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-V10 | Vertical Shaft V10 | TBD | 38.7204 | 37 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 584200.5922 | 584200.5922 |  | 55 mT B≤ 73 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-V11 | Vertical Shaft V11 | TBD | 39.4231 | 37 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 584200.5922 | 584200.5922 |  | 55 mT B≤ 73 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-V12 | Vertical Shaft V12 | TBD | 39.4259 | 37 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 584200.5922 | 584200.5922 |  | 55 mT B≤ 73 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-V13 | Vertical Shaft V13 | TBD | 39.4259 | 37 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 584200.5922 | 584200.5922 |  | 55 mT B≤ 73 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-V14 | Vertical Shaft V14 | TBD | 39.4259 | 37 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 584205.8366 | 584205.8366 |  | 55 mT B≤ 73 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-V15 | Vertical Shaft V15 | TBD | 39.4259 | 37 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 584200.5922 | 584200.5922 |  | 55 mT B≤ 73 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-V16 | Vertical Shaft V16 | TBD | 39.4259 | 37 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 584200.5922 | 584200.5922 |  | 55 mT B≤ 73 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-V17 | Vertical Shaft V17 | TBD | 39.4259 | 37 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 609500.4536 | 609500.4536 |  | 55 mT B≤ 73 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-V18 | Vertical Shaft V18 | TBD | 30.579 | 29 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 609500.4536 | 609500.4536 |  | 55 mT B≤ 73 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-VNE | NE Cable Tray Shaft | TBD | 20.59 | 20 | 11-Gallery area | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-62 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 31.042 | 31.042 |  | 4 mT B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-VNW | NW Cable Tray Shaft | TBD | 28.74 | 27 | 11-Gallery area | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-61 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 3093.112 | 3093.112 |  | 4 mT B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-VSE | SE Cable Trays and HVAC Shaft | TBD | 44.29 | 42.0755 | 11-Gallery area | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-57 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 31 | 31 |  | 5 mT B≤ 10 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B1-VSW | SW Cable Trays and HVAC Shaft | TBD | 61.64 | 59 | 11-Gallery area | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-56 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 31.042 | 31.042 |  | 6 mT B≤ 9 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2-01 | TCWS Drain Tanks | 380.44 | 2111.78 | 1351.539 | 11-Drain tank Room | No |  | yes (***) | yes (***) | Stainless Steel Liner |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 300 or 100 000 300 if no air pathway following a LOCA in the vault (design dependant), 100 000 if air pathway | 130 if air pathway from the vault (design dependant), NA if not | 1 if air pathway to the vault; 0.055 else (design dependant) | 0 | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | Yes | 100000 | 125 | 1 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 0 or 20000 (0 if no air pathway, 20 000 if air pathway) | 100 |  | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-01 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-01 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C3-DS | 1 | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 909.3094 | 1178.1894 |  | 6 mT B≤ 17 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | NA (no Be) | LPZ 1
11 | 11-B2-02E | Basement Gallery E | 682.86 | 3911.84 | 2894.762 | 11-Gallery area | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-63 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Orange | 3399.5309 | 3399.5309 |  | 6 mT B≤ 126 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2-02N | Basement Gallery N | 971.5 | 3797.2 | 2809.928 | 11-Gallery area | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-63 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Orange | 3399.5309 | 3399.5309 |  | 14 mT B≤ 126 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2-02S | Basement Gallery S | 1203.89 | 4760.42 | 3522.711 | 11-Gallery area | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-63 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Orange | 3399.5309 | 3399.5309 |  | 14 mT B≤ 126 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2-02W | Basement Gallery W | 712.04 | 3999.01 | 2959.267 | 11-Gallery area | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-63 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Orange | 3399.5309 | 3399.5309 |  | 6 mT B≤ 126 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2-04NE (nota 28) | Room SIC-1 North East Corner | 9.91 | 29.63 | 28 | 11-PIC cubicle rooms | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 () |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 () | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 () | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | Yes | 20000 | 0, 1, 2 |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-08 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-1 (7) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Orange | 67.9884 | 67.9884 |  | 4 mT B≤ 6 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2-04SE (nota 28) | Room SIC-1 South East Corner | 11.08 | 33.26 | 32 | 11-PIC cubicle rooms | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 () |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 () | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 () | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | Yes | 20000 | 0, 1, 2 |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-74 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-1 (7) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Orange | 67.9884 | 67.9884 |  | 10 mT B≤ 15 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2-05NE (nota 28) | Room SIC-2 North East Corner | 11.2 | 33.5 | 34 | 11-PIC cubicle rooms | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 () |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 () | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 () | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | Yes | 20000 | 0, 1, 2 |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-79 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-2 (7) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Orange | 67.9884 | 67.9884 |  | 5 mT B≤ 10 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2-05NW (nota 28) | Room SIC-2 North West Corner | 23.76 | 71.47 | 68 | 11-PIC cubicle rooms | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 () |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 () | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 () | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | Yes | 20000 | 0, 1, 2 |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-09 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-2 (7) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Orange | 67.9884 | 67.9884 |  | 5 mT B≤ 7 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2-05SE (nota 28) | Room SIC-2 South East Corner | 24.19 | 72.16 | 69 | 11-PIC cubicle rooms | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 () |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 () | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 () | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | Yes | 20000 | 0, 1, 2 |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-75 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-2 (7) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Orange | 1.3598 | 1.3598 |  | 7 mT B≤ 13 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2-LFT | Tokamak Cargo Lift | 80.32 | 634.58 | 603 | 11-Cargo-lift area | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (insulated) | 11-FS-07 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 1344.6891 | 1344.6891 |  | 6 mT B≤ 17 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-B2M-01E | Lower Pipe Chase E | 204.05 | 703.98 | 669 | 1114-Vault | No |  | yes (***) | yes (***) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Orange | 832606.3472 | 832606.3472 |  | 52 mT B≤ 143 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2M-01N | Lower Pipe Chase N | 273.44 | 943.39 | 896 | 1114-Vault | No |  | yes (***) | yes (***) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Orange | 832606.3472 | 832606.3472 |  | 52 mT B≤ 143 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2M-01S | Lower Pipe Chase S | 261.83 | 903.32 | 858 | 1114-Vault | No |  | yes (***) | yes (***) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Orange | 832606.3472 | 832606.3472 |  | 52 mT B≤ 143 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2M-01W | Lower Pipe Chase W | 207.27 | 715.09 | 679 | 1114-Vault | No |  | yes (***) | yes (***) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Orange | 832606.3472 | 832606.3472 |  | 52 mT B≤ 143 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2M-SN | North Stairwell | TBD | TBD | TBD | 11-Gallery area | No |  | yes (***) | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-63 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Orange | 95220.2289 | 95220.2289 |  | 30 mT B≤ 40 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2M-SS | South Stairwell | TBD | TBD | TBD | 11-Gallery area | No |  | yes (***) | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-63 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Orange | 95220.1094 | 95220.1094 |  | 30 mT B≤ 40 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2M-SW | West Stairwell | TBD | TBD | TBD | 11-Gallery area | No |  | yes (***) | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-63 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Orange | 95220.264 | 95220.264 |  | 30 mT B≤ 40 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2-PIT | Cryostat Room | 437.97 | 2750.18 | 2035.133 | 11-Gallery area | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | -60 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-63 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 0.10929 | 0.10929 |  | B > 150 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2-SU1 | Sump 1 | 45.85 | 77.95 | 74 | 1114-Vault | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Orange | 3399.5309 | 3399.5309 |  | 48 mT B≤ 126 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2-VNE | NE Cable Tray Shaft | 4 | 22.2 | 21 | 11-Gallery area | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-62 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 0.15577 | 0.15577 |  | 4 mT B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2-VNW | NW Cable Tray Shaft | 5.58 | 30.97 | 29 | 11-Gallery area | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-61 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 0.15731 | 0.15731 |  | 4 mT B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2-VSE | SE Cable Trays and HVAC Shaft | 8.6 | 47.73 | 45 | 11-Gallery area | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-57 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 0.15577 | 0.15577 |  | 7 mT B≤ 8 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-B2-VSW | SW Cable Trays and HVAC Shaft | 11.97 | 66.43 | 63 | 11-Gallery area | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-56 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 0.15577 | 0.15577 |  | 6 mT B≤ 8 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-02E | Equatorial Gallery E | 824.3105 | 3699.605 | 2737.708 | 11-Gallery area | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-07 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-64 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 4311.356 | 4311.356 |  | 6 mT B≤ 38 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-02S | Equatorial Gallery S | 620.6025 | 2841.959 | 2103.05 | 11-Gallery area | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-07 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-64 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 4311.356 | 4311.356 |  | 15 mT B≤ 38 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-02W | Equatorial Gallery W | 567.8936 | 2666.995 | 1973.577 | 11-Gallery area | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-07 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-64 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 4311.356 | 4311.356 |  | 6 mT B≤ 38 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-04NE (nota 28) | Room SIC-1 North East Corner | 24.87 | 74.4375 | 70.7156 | 11-PIC cubicle rooms | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req, with specific conductive quality |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 () |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 () | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 () | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | Yes | 20000 | 0, 1, 2 |  | 11-DS-07 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-67 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-1 (7) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 499.2886 | 499.2886 |  | 4 mT B≤ 7 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-05NW (nota 28) | Room SIC-2 North West Corner | 34.95 | 104.4945 | 99.2698 | 11-PIC cubicle rooms | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req, with specific conductive quality |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 () |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 () | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 () | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | Yes | 20000 | 0, 1, 2 |  | 11-DS-07 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-68 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-2 (7) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 499.2886 | 499.2886 |  | 5 mT B≤ 8 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-ANB | NB Cell Airlock | 2.25 | 4.95 | 5 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 0.055 (3) | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 0.055 | 0 | Yes | 60000 | 145 | extrapolation 2E4KSJ | 0 | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | yes | 100000 | 345 | 1 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-06 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-95 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 82800.1091 | 82800.1091 |  | 18 mT B≤ 21 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-C01 | Port Cell C01 | 56.3652 | 266.7144 | 253.3786 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-61 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-30 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 31.9651 | 31.9651 |  | 50 mT B≤ 218 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-C02 | Port Cell C02 | 57.1524 | 269.8046 | 256.3144 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-62 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-29 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 54.8489 | 54.8489 |  | 50 mT B≤ 218 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-C03 | Port Cell C03 | 51.5667 | 242.3522 | 230.2345 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-63 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-28 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 624.3372 | 624.3372 |  | 50 mT B≤ 218 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-C08 | Port Cell C08 | 70.802 | 332.4764 | 315.8526 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-68 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-41 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 624.3372 | 624.3372 |  | 50 mT B≤ 218 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-C09 | Port Cell C09 | 54.2601 | 256.6531 | 243.8204 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-69 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-40 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3372 | 124.3372 |  | 50 mT B≤ 218 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-C10 | Port Cell C10 | 56.2354 | 266.3108 | 252.9953 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-70 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-39 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3372 | 124.3372 |  | 50 mT B≤ 218 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-C11 | Port Cell C11 | 58.1244 | 275.0209 | 261.2698 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-71 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-38 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3372 | 124.3372 |  | 50 mT B≤ 218 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-C12 | Port Cell C12 | 48.9054 | 230.2996 | 218.7846 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-72 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-37 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 624.3372 | 624.3372 |  | 50 mT B≤ 218 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-C13 | Port Cell C13 | 61.1929 | 290.272 | 275.7584 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-73 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-36 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3372 | 124.3372 |  | 50 mT B≤ 218 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-C14 | Port Cell C14 | 56.9802 | 269.7 | 256.215 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-74 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-35 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3372 | 124.3372 |  | 50 mT B≤ 218 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-C15 | Port Cell C15 | 61.1711 | 290.1485 | 275.6411 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-75 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-34 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3372 | 124.3372 |  | 50 mT B≤ 218 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-C16 | Port Cell C16 | 57.3622 | 271.3215 | 257.7554 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-76 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-33 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 1778.4159 | 1778.4159 |  | 50 mT B≤ 218 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-C17 | Port Cell C17 | 49.034 | 230.4501 | 218.9276 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-77 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-32 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 1978.4159 | 1978.4159 |  | 26 mT B≤ 218 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-C18 | Port Cell C18 | 62.1367 | 295.1039 | 280.3487 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-78 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-31 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 424.3372 | 424.3372 |  | 50 mT B≤ 218 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-CNB | NB Cell | 1114.387 | 5142.382 | 4165.329 | 11-NB Cell | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 0.055 | 0 | Yes | 60000 | 145 | extrapolation 2E4KSJ | 0 | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | yes | 100000 | 345 | 1 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-06 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-05 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 82815.319 | 82815.319 |  | 6 mT B≤ 173 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-LFT | Tokamak Cargo Lift | TBD | 440.19 | 418 | 11-Cargo-lift area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (insulated) | 11-FS-07 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 310.7242 | 310.7242 |  | 6 mT B≤ 18 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-PNW | NW Cryo-Line Shaft | TBD | 51.19 | 49 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 |  | Yes (metallic) | 11-FS-59 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 3679.4905 | 3679.4905 |  | 5 mT B≤ 6 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L1-PSW | SW Cryo-Line Shaft | TBD | 45.6484 | 43 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 |  | Yes (metallic) | 11-FS-63 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 25.8 | 25.8 |  | 7 mT B≤ 10 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-V01 | Vertical Shaft V01 | TBD | 34.5523 | 33 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | NA (no Be) | LPZ 1
11 | 11-L1-V02 | Vertical Shaft V02 | TBD | 31.3385 | 30 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 7.1548 | 7.1548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-V03 | Vertical Shaft V03 | TBD | 40.4022 | 38 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 7.3548 | 7.3548 |  | 56 mT B≤ 75 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | NA (no Be) | LPZ 1
11 | 11-L1-V08 | Vertical Shaft V08 | TBD | 40.4 | 38 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 7.3548 | 7.3548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-V09 | Vertical Shaft V09 | TBD | 40.4478 | 38 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-V10 | Vertical Shaft V10 | TBD | 39.6791 | 38 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-V11 | Vertical Shaft V11 | TBD | 40.4022 | 38 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-V12 | Vertical Shaft V12 | TBD | 40.4022 | 38 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 7.3548 | 7.3548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-V13 | Vertical Shaft V13 | TBD | 40.4022 | 38 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-V14 | Vertical Shaft V14 | TBD | 40.4022 | 38 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-V15 | Vertical Shaft V15 | TBD | 40.4022 | 38 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-V16 | Vertical Shaft V16 | TBD | 40.4022 | 38 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 1361.2335 | 1361.2335 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-V17 | Vertical Shaft V17 | TBD | 40.4022 | 38 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 611800.9736 | 611800.9736 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-V18 | Vertical Shaft V18 | TBD | 31.3589 | 30 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 611800.7736 | 611800.7736 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-VNE | NE Cable Tray Shaft VNE | TBD | 21.92 | 21 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-62 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 9.9858 | 9.9858 |  | 6 mT B≤ 7 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-VNW | NW Cable Tray Shaft VNW | TBD | 30.5852 | 29 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-61 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 3.8041 | 3.8041 |  | 4 mT B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-VSE | SE Cable Trays and HVAC Shaft | TBD | 47.128 | 44.7716 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-57 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 25 | 25 |  | 5 mT B≤ 10 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L1-VSW | SW Cable Trays and HVAC Shaft | TBD | 65.5956 | 62 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-56 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 280.7825 | 280.7825 |  | 6 mT B≤ 9 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L2-01 | NB Cell Mezzanine | TBD | 5886 | 4767.66 | 11-NB Cell | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 0.055 | 0 | Yes | 60000 | 145 | extrapolation 2E4KSJ | 0 | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | Yes | 100000 | 345 | 1 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-06 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-05 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 82805.6939 | 82805.6939 |  | 53 mT B≤ 200 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L2-02E | Upper Port Gallery E | 789 | 3500 | 2590 | 11-Gallery area | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-65 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 2284.0542 | 2284.0542 |  | 6 mT B≤ 37 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L2-02S | Upper Port Gallery S | 624 | 2734 | 2023.16 | 11-Gallery area | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-65 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 2277.3487 | 2277.3487 |  | 14 mT B≤ 37 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L2-02W | Upper Port Gallery W | 598 | 2635 | 1949.9 | 11-Gallery area | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-65 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 2277.3487 | 2277.3487 |  | 6 mT B≤ 37 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L2-04SW (nota 28) | Room SIC-1 South West Corner | 18 | 65 | 61.75 | 11-PIC cubicle rooms | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req, with specific conductive quality |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 () |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 () | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 () | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | Yes | 20000 | 0, 1, 2 |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-69 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-1 (7) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 567.8885 | 567.8885 |  | 10 mT B≤ 11 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L2-05SE (nota 28) | Room SIC-2 South East Corner | 31 | 93 | 88.35 | 11-PIC cubicle rooms | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req, with specific conductive quality |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 () |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 () | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 () | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | Yes | 20000 | 0, 1, 2 |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-70 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-2 (7) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 568.0226 | 568.0226 |  | 10 mT B≤ 11 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L2-C01 | Port Cell C01 | 56 | 253 | 240.35 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-81 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-42 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3375 | 124.3375 |  | 49 mT B≤ 305 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-L2-C02 | Port Cell C02 | 57 | 259 | 246.05 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-82 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-43 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3375 | 124.3375 |  | 49 mT B≤ 305 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-L2-C03 | Port Cell C03 | 53 | 238 | 226.1 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-83 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-44 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3372 | 124.3372 |  | 49 mT B≤ 305 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-L2-C08 | Port Cell C08 | 61 | 277 | 263.15 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-88 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-45 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3372 | 124.3372 |  | 49 mT B≤ 305 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-L2-C09 | Port Cell C09 | 54 | 246 | 233.7 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-89 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-46 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3372 | 124.3372 |  | 49 mT B≤ 305 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-L2-C10 | Port Cell C10 | 56 | 255 | 242.25 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-90 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-47 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3372 | 124.3372 |  | 49 mT B≤ 305 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-L2-C11 | Port Cell C11 | 57 | 260 | 247 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-91 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-48 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3372 | 124.3372 |  | 49 mT B≤ 305 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-L2-C12 | Port Cell C12 | 56 | 255 | 242.25 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-92 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-49 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3372 | 124.3372 |  | 49 mT B≤ 305 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-L2-C13 | Port Cell C13 | 57 | 256 | 243.2 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-93 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-50 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3372 | 124.3372 |  | 49 mT B≤ 305 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-L2-C14 | Port Cell C14 | 56 | 255 | 242.25 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-94 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-51 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3372 | 124.3372 |  | 49 mT B≤ 305 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-L2-C15 | Port Cell C15 | 56 | 255 | 242.25 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-95 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-52 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3372 | 124.3372 |  | 49 mT B≤ 305 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-L2-C16 | Port Cell C16 | 57 | 258 | 245 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-96 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-53 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 1478.4159 | 1478.4159 |  | 49 mT B≤ 305 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-L2-C17 | Port Cell C17 | 57 | 256 | 243.2 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-97 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-54 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 1478.4159 | 1478.4159 |  | 49 mT B≤ 305 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-L2-C18 | Port Cell C18 | 55 | 247 | 234.65 | 11-Port Cell | No |  | yes (*) | yes (**) | Water tight lining, decontamination req + slope |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 |  | 1 | 0 | No |  |  |  |  | Yes | 60000 | 145 | 14.2 | 0 | No |  |  |  |  | Yes | -24 | 16 | 16 | 34 | NA | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-98 | 2+2 (but no HVAC) | PIC/SIC-1 |  | Yes (metallic) | 11-FS-55 | PIC/SIC-1 but no HVAC | REI - 120 | PIC/SIC-1 | automatic fire suppression system | PIC/SIC-2 |  | C3-DS | extrapolation 2E4KSJ | C3DSHVAC fix or mobile | extrapolation 2E4KSJ | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC 2 but no HVAC | 2 |  | Red | Yellow | Red | 124.3372 | 124.3372 |  | 49 mT B≤ 305 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | Be CZ | LPZ 1
11 | 11-L2-LFT | Tokamak Cargo Lift | TBD | 416 | 395 | 11-Cargo-lift area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (insulated) | 11-FS-07 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 1344.6891 | 1344.6891 |  | 6 mT B≤ 18 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L2-PNW | NW Cryo-Line Shaft | TBD | 53 | 50 | 11-Gallery area | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-59 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 764.1576 | 764.1576 |  | 56 mT B≤ 75 mT | ZDC | No zone | Be CZ | LPZ 1
11 | 11-L2-PSW | SW Cryo-Line Shaft | TBD | 47 | 45 | 11-Gallery area | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-63 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 5.5209 | 5.5209 |  | 56 mT B≤ 75 mT | ZDC | No zone | NA (no Be) | LPZ 1
11 | 11-L2-V01 | Vertical Shaft V01 | TBD | 37 | 35.15 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | NA (no Be) | LPZ 1
11 | 11-L2-V02 | Vertical Shaft V02 | TBD | 33 | 31.35 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L2-V03 | Vertical Shaft V03 | TBD | 43 | 40.85 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | NA (no Be) | LPZ 1
11 | 11-L2-V08 | Vertical Shaft V08 | TBD | 43 | 40.85 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L2-V09 | Vertical Shaft V09 | TBD | 43 | 40.85 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L2-V10 | Vertical Shaft V10 | TBD | 42 | 39.9 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L2-V11 | Vertical Shaft V11 | TBD | 43 | 40.85 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L2-V12 | Vertical Shaft V12 | TBD | 43 | 40.85 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L2-V13 | Vertical Shaft V13 | TBD | 43 | 40.85 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L2-V14 | Vertical Shaft V14 | TBD | 43 | 40.85 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L2-V15 | Vertical Shaft V15 | TBD | 43 | 40.85 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 6.8548 | 6.8548 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L2-V16 | Vertical Shaft V16 | TBD | 43 | 40.85 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 1360.9335 | 1360.9335 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L2-V17 | Vertical Shaft V17 | TBD | 43 | 40.85 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 611800.4736 | 611800.4736 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L2-V18 | Vertical Shaft V18 | TBD | 33 | 31.35 | 1114-Vault | No |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 611800.4736 | 611800.4736 |  | 56 mT B≤ 75 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L2-VNE | NE Cable Tray Shaft | TBD | 21 | 20 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-62 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 5.5209 | 5.5209 |  | 5 mT B≤ 7 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L2-VNW | NW Cable Tray Shaft | TBD | 29 | 27 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-61 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 764.1576 | 764.1576 |  | 4 mT B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L2-VSE | SE Cable Trays and HVAC Shaft | TBD | 45 | 45 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-57 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 58.4656 | 58.4656 |  | 6 mT B≤ 7 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L2-VSW | SW Cable Trays and HVAC Shaft | TBD | 62 | 59 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-56 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 58.4656 | 58.4656 |  | 6 mT B≤ 8 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L3-01 | HV Deck & CTB Area North | 827.3 | 6580.19 | 6327 | 11-Gallery area | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-09 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-06 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 23564.9773 | 23564.9773 |  | 6 mT B≤ 39 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | NA (no Be) | LPZ 1
11 | 11-L3-02E | TCWS Area East | 722.12 | 3888.82 | 10367 | 1114-Vault | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 198841.7997 | 198841.7997 |  | 4 mT B≤ 125 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | NA (no Be) | LPZ 1
11 | 11-L3-02S | CTB and TSCS Area South | 482.36 | 2916.03 | 2827 | 11-Gallery area | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-09 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-06 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 23614.8898 | 23614.8898 |  | 6 mT B≤ 39 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L3-02W | Cryo-Distribution Area | 718.21 | 8401.8 | 7998 | 11-Gallery area | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-09 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-06 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 23564.9477 | 23564.9477 |  | 4 mT B≤ 43 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L3-04NE (nota 28) | Room SIC-1 North East Corner | 9.9 | 29.19 | 29 | 11-PIC cubicle rooms | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req, with specific conductive quality |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | Yes | 100000 | 0, 1, 2 |  | 11-DS-04 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-72 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-1 (7) |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 117.4968 | 117.4968 |  | 5 mT B≤ 6 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L3-04SW (nota 28) | Room SIC-1 South West Corner | 10.26 | 26.27 | 28 | 11-PIC cubicle rooms | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req, with specific conductive quality |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | Yes | 300 () |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 () | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 () | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | Yes | 20000 | 0, 1, 2 |  | 11-DS-09 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-71 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-1 (7) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 471.2986 | 471.2986 |  | 7 mT B≤ 10 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L3-03E | Upper pipe chase E | 659.88 | 4825.85 | TBD | 1114-Vault | No |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 23564.9773 | 23564.9773 |  | B > 150 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L3-03N | Upper pipe chase N | 139.76 | 1114.32 | TBD | 1114-Vault | No |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 & 11-FS-06 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 23564.9773 | 23564.9773 |  | B > 150 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L3-03S | Upper pipe chase S | 191.59 | 1210.96 | TBD | 1114-Vault | No |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 & 11-FS-06 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 23564.9773 | 23564.9773 |  | B > 150 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L3-03W | Upper pipe chase W | 175.61 | 1342.41 | TBD | 1114-Vault | No |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes (9) | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 & 11-FS-06 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 23564.9773 | 23564.9773 |  | B > 150 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L3-LFT | Tokamak Cargo Lift | TBD | 667.34 | 633 | 11-Cargo-lift area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (insulated) | 11-FS-07 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 309.6891 | 309.6891 |  | 6 mT B≤ 17 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L3-VNE | NE Cable Tray Shaft | TBD | 33.2 | 32 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-62 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 117.5231 | 117.5231 |  | 5 mT B≤ 7 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L3-VNW | NW Cable Tray Shaft | TBD | 69.76 | 66 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-61 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 1.0951 | 1.0951 |  | 4 mT B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L3-VSE | SE Cable Trays and HVAC Shaft | TBD | 71.38 | 63 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-57 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 118 | 118 |  | 6 mT B≤ 8 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L3-VSW | SW Cable Trays and HVAC Shaft | TBD | 149.62 | 142 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-56 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 1.1217 | 1.1217 |  | 6 mT B≤ 8 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L4-01N | Crane Hall North | 1310.71 | 61886.59 | 54980 | NA | No* |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | No |  |  |  |  | No |  |  |  | NA | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | NA | NA |  |  | Yes (metallic) | FZ see ARFI Room Book | NA | FZ - see ARFI Room Book | NA | Manual extinction fix or not (9) | SR |  | NA | 1 | NA | 1 | NA | 1 | yes |  | NA | NA |  | Red | Blue | Blue | 0.109 | 0.109 |  | 16 mT B≤ 67 mT | ZDC | No zone | NA (no Be) | LPZ 1
11 | 11-L4-01S | Crane Hall South | 982.17 | 50155.26 | 45462 | NA | No* |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | No |  |  |  |  | No |  |  |  | NA | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | NA | NA |  |  | Yes (metallic) | FZ see ARFI Room Book | NA | FZ - see ARFI Room Book | NA | Manual extinction fix or not (9) | SR |  | NA | 1 | NA | 1 | NA | 1 | yes |  | NA | NA |  | Red | Blue | Blue | 0.109 | 0.109 |  | 17 mT B≤ 75 mT | ZDC | No zone | NA (no Be) | LPZ 1
11 | 11-L4-02 | Top bioshield | 877.81 | 34496.6 | 28957 | NA | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | No |  |  |  |  | No |  |  |  | NA | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | NA | NA |  |  | Yes (metallic) | FZ see ARFI Room Book | NA | FZ - see ARFI Room Book | NA | Manual extinction fix or not (9) | SR |  | NA | NA | NA | NA | NA | NA | yes |  | NA | NA |  | Red | Blue | Blue | 0.10929 | 0.10929 |  | 75 mT B≤ 133 mT | ZDC | No zone | NA (no Be) | LPZ 1
11 | 11-L4-04 | TCWS/CVCS/TBM area | 1186 | 17564.05 | 16844 | 1114-Vault | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 3348803.5534 | 3348803.5534 |  | 4 mT B≤ 67 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L4-LFT | Tokamak Cargo Lift | TBD | 1167.02 | 1145 | 11-Cargo-lift area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (insulated) | 11-FS-07 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 309.6891 | 309.6891 |  | 6 mT B≤ 14 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-L4-VNE | NE Cable Tray Shaft | TBD | 60 | 57 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-62 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 231 | 231 |  | 5 mT B≤ 7 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L4-VNW | NW Cable Tray Shaft | TBD | TBD | TBD | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-61 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 58.4656 | 58.4656 |  | 5 mT B≤ 10 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L4-VSE | SE Cable Trays and HVAC Shaft | TBD | 129 | 114 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-57 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 118 | 118 |  | 6 mT B≤ 7 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L4-VSW | SW Cable Trays and HVAC Shaft | TBD | TBD | TBD | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-56 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 58.4656 | 58.4656 |  | 5 mT B≤ 10 mT | ZDN | No zone | NA (no Be) | LPZ 1
TBD | 11-L5-01 | VV Pressure Suppression Tank | TBD | TBD | 7368 | 11-Gallery area | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [5 empty] | Yes |  | No |  |  |  | 11-DS-10 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-03 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | (17) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 2 (10) |  | Red | Blue | Blue | 0.112 | 54 |  | 5 mT B≤ 35 mT | ZDN | no zone except zone 2 with 1,5 m around specific capacities | NA (no Be) | LPZ 1
11 | 11-L5-ASW | Air Lock South West | TBD | TBD | TBD | 111474-Air-lock | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 (3) | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-10 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 11-FS-701 (nota 26) | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | PIC/SIC2 |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 2 (10) |  | Red | Blue | Blue | 0.10929 | 0.10929 |  | 5 mT B≤ 35 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L5-VNW | NW Cable Tray Shaft | TBD | TBD | 95 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-61 (nota 26) | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 0.109 | 0.109 |  | 4 mT B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-L5-VSW | SW Cable Tray Shaft | TBD | TBD | 172 | 11-Gallery area | Yes |  | No | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-56 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 0.109 | 0.109 |  | 5 mT B≤ 7 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-R1-01E (nota 25) | Load center, safety chiller units | TBD | TBD | TBD | NA | (21) |  | yes (*) | No | Avoidance of water infiltration to the nuclear building |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | FS different from 14-R1-03 (21) | Nota (21) | Nota (21) | PIC/SIC-1 | Extinction fix or not (9) | (17) |  | NA | 0 | NA | 0 | NA | 0 | NA |  | NA | NA |  | Red (forbiden access but requirement to add shielding) | Green | Green | 9.9858 | 9.9858 |  | TBD | ZDC | No zone | NA (no Be) | LPZ 1
11 | 11-R1-01W (nota 25) | West roof | TBD | TBD | TBD | N/A | No* |  | yes (*) | No | Avoidance of water infiltration to the nuclear building |  | No |  |  |  |  | No |  |  |  |  | No | [53 empty] | No |  |  |  | N/A | N/A | N/A |  | Yes (metallic) | N/A
11 | 11-R1-02 | Lift Motor Room (U) | TBD | TBD | TBD | 11-Cargo-lift area | Yes |  | yes (*) | No | Epoxy coating with decontamination req |  | Yes | +-5000 | Eurocode 2h | interpolated from 2E4KSJ | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (insulated) | 11-FS-07 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (11) | PIC/SIC-1 |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 1 |  | Red | Blue | Yellow | 0.109 | 0.109 |  | 5 mT B≤ 10 mT | ZDN | No zone | Be CZ | LPZ 1
11 | 11-R1-A1 (nota 22) | Airlock to lift 1 | TBD | TBD | 90 | 111474-Air-lock | Yes |  | yes (*) | No | Epoxy coating with decontamination req |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 (3) | Yes | 1,05 | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-78 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | PIC/SIC2 |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Blue | Green | 0.10929 | 0.10929 |  | 5 mT B≤ 10 mT | ZDN | No zone | NA (no Be) | LPZ 1
11 | 11-R1-03 (nota 22) | Corridor | TBD | TBD | TBD | N/A | yes |  | yes (*) | yes (**) | Water tight lining, decontamination req | [10 empty] | 1 | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | TBD | TBD | TBD |  | TBD | TBD | TBD | TBD | TBD | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Blue | Yellow | 309.6891 | 309.6891 |  | 5 mT B≤ 10 mT | ZDC | No zone | NA (no Be) | LPZ 1
11 | 11-R1-04A (nota 22, 28) | Room SIC-1 North | TBD | TBD | TBD | 11-PIC cubicle rooms / 111474-Air-lock | yes |  | yes (*) | yes (**) | Water tight lining and decontamination req, with specific conductive quality |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | Yes | 20000 | 0, 1, 2 |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-77 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-1 (7) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Blue | Yellow | 309.6891 | 309.6891 |  | 5 mT B≤ 10 mT | ZDC | No zone | NA (no Be) | LPZ 1
11 | 11-R1-04B (nota 22, 28) | Room SIC-1 South | TBD | TBD | TBD | 11-PIC cubicle rooms / 111474-Air-lock | yes |  | yes (*) | yes (**) | Water tight lining and decontamination req, with specific conductive quality |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 1 | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | Yes | 20000 | 0, 1, 2 |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 11-FS-76 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-1 (7) |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Blue | Yellow | 309.6891 | 309.6891 |  | 5 mT B≤ 10 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-01 | Power Distribution | 8.71 | 41.2045 | 39.1443 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) (13) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-21 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-02 | Corridor | 13.45 | 55.57 | 53 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (13) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-03 | Corridor | 37.51 | 105.0448 | 99.7926 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-25 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-04 | Room name IO restricted | 43.31 | 205.4485 | 195.1761 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-55 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-05 | Corridor | 145.825 | 478.4587 | 454.5358 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-32 (nota 26) | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-05A | Control & CODAC Cubicles | 14.95 | 69.6275 | 66.1461 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | N/A | 0, 1, 2 |  | No specified LR | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-72 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-06 | Corridor | 181.87 | 516.62 | 490.789 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-32 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-06A | Control & CODAC Cubicles | 23.925 | 111.6263 | 106.0449 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | N/A | 0, 1, 2 |  | No specified LR | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-71 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-07 | Corridor | 76.825 | 234.3163 | 222.6004 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-33 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-07A (nota 28) | SIC-2 train B cubicles Room | 45.15 | 211.29 | 200.7255 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining and decontamination req, with specific conductive quality |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | N/A | 0, 1, 2 |  | No specified LR | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | Yes | -5000, +10000 | 0, 1, 2 |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-30 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-2 (7) |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤6.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-08 | Corridor | 18.645 | 88.5637 | 84.1356 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-52 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-09 | Corridor | 7.904 | 37.544 | 35.6668 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-10 | Power Distribution | 8.525 | 40.4937 | 38.4691 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | N/A | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-22 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-11 | Ventilation Systems & Cubicles | 31.477 | 149.5157 | 142.04 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-56 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5≤B≤6.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-12 | Corridor | 6.5 | 19.82 | 19 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-13 | Corridor | 9.802 | 27.4456 | 26.0733 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-20 | Room name IO restricted | TBD | 123.795 | 111.4155 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) | 0, 1, 2 |  | 1 (for FS) | Yes | 1,2 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-11 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-02 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-B1-21 | Room name IO restricted | TBD | 313.0381 | 281.7343 | 14-Proccess room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) | 0, 1, 2 |  | 1 (for FS) | Yes | 3,5 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-12 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-01 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6.5 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-B1-22 | Room name IO restricted | 83.795 | 397.13 | 357.417 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) | 0, 1, 2 |  | 1 (for FS) | Yes | 1,75 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-13 | 2+2 (mutualization possible) | PIC/SIC-1 |  | Yes (insulated) | 14-FS-03 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤7.5 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-B1-22A | Room name IO restricted | 49.145 | 233.4388 | 210.0949 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,75 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-13 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-81 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | B≤11 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-B1-23 | Room name IO restricted | 145.98 | 692.9925 | 623.6932 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,75 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-14 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-95 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | B≤15mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-B1-24 | Room name IO restricted | 141.15 | 669.81 | 602.829 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,75 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-15 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-10 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | B≤15mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-B1-25 | Room name IO restricted | 94.2925 | 447.8894 | 403.1004 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) | 0, 1, 2 |  | 1 (for FS) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-16 | 2+2 (mutualization possible) | PIC/SIC-1 |  | Yes (insulated) | 14-FS-05 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤12mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-B1-26 | Room name IO restricted | 32.205 | 152.8215 | 137.5394 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-16 | 2+2 (mutualization possible) | PIC/SIC-1 |  | Yes (insulated) | 14-FS-88 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | B≤15.5mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-B1-27 | Room name IO restricted | 64.2925 | 305.3894 | 274.8504 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-16 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-06 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | 7.5 mT ≤B≤ 15 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-28 | Room name IO restricted | 76.5525 | 363.4721 | 327.1249 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) | 0, 1, 2 |  | 1 (for FS) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-18 | 2+2 (mutualization possible) | PIC/SIC-1 |  | Yes (insulated) | 14-FS-07 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤7.5 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-B1-28A | Room name IO restricted | 30.69 | 145.7775 | 131.1998 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) | 0, 1, 2 |  | 1 (for FS) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-18 | 2+2 (mutualization possible) | PIC/SIC-1 |  | Yes (insulated) | 14-FS-83 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 9.5 mT ≤B≤ 7.5mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-B1-29 | Room name IO restricted | 65.655 | 311.8615 | 280.6753 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-18 | 2+2 (mutualization possible) | PIC/SIC-1 |  | Yes (insulated) | 14-FS-08 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | 10.5 mT ≤B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-B1-A1 | Airlock to Tokamak Building | 7.41 | 20.74 | 20 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | No |  | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | No | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-05 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 14-FS-101 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 31.042 | 31.042 |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | Be CZ | LPZ 1
14 | 14-B1-A2 | Airlock to Tritium Building | 9.7378 | 27.266 | 25.9027 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-102 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-A3 | Airlock to Tritium Building | 8.565 | 26.1232 | 24.8171 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-103 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-A4 | Airlock to Tokamak Building | 7.41 | 22.6005 | 21 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | No |  | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | No | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-05 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 14-FS-104 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 31.042 | 31.042 |  | 7 mT ≤B≤ 10 mT | ZDC | No zone | Be CZ | LPZ 1
14 | 14-B1-A5 | Airlock | 4.08 | 11.424 | TBD | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-50 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-105 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Green (if wall near the TKM lift is considered for shielding) | 31.042 | 31.042 |  | 7.5≤ B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-B1-L1 | North Personnel Lift Tokamak Building | TBD | 18.9 | 18 | 1474-Stairway | No |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-L2 | North Personnel Lift Tritium Building | TBD | 18.9 | 18 | 1474-Stairway | No |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-16 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-L3 | South Personnel Lift | TBD | 18.9 | 18 | 1474-Stairway | No |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5≤ B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-LFT | Large Lift | TBD | 127.5488 | 121.1713 | 111474-Air-lock (or process if rad materials transported) | No |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR (if no radioactive materials; otherwise, 4.1) (5) | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS (if no radioactive materials, otherwise DS sector) (5) | 1+1 ( if no radioactive materials otherwise 2+2 ) |  |  | Yes (metallic) | 14-FS-52 | PIC/SIC-2 if no radioactive materials (otherwise PIC/SIC 1 ) (5) | REI - 120 | PIC/SIC-2 if no radioactive materials (otherwise PIC/SIC 1 ) (5) | Manual extinction fix or not (9) | SR if no radioactive materials (otherwise PIC/SIC-2) (5) |  | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-S1 | North Stairway Tokamak Building | 17.5275 | 92.0194 | 87.4184 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-S2 | North Stairway Tritium Building | 31.871 | 159.0044 | 151.0542 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-16 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-S3 | South Stairway Tokamak and Tritium Building | 17.67 | 92.7675 | 88.1291 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1M-TG1 | North Tokamak Technical Gallery | 69.1 | 114.015 | 108.3142 | 14-Facility rooms _by level (12) | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-32 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1M-TG2 | North Tritium Technical Gallery | 103.66 | 145.12 | 145.12 | 14-Facility rooms _by level (12) | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-32 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-V1 | Ventilation Systems Shaft | 33.68 | 192.425 | 182.8038 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-50 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-24 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Green | Green (if wall near the TKM lift is considered for shielding) | 31.042 | 31.042 |  | 7.5≤ B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-B1-V3 | Cable Tray Shaft | TBD | 32.76 | 31.122 | 14-Facility rooms _by level | No |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-21 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B1-V4 | Piping Shaft | TBD | 39.37 | 37 | 14-Process room on DS | No |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-51 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-23 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction ( room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤6 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-B1-V5 | Cable Tray Shaft | TBD | 32.4844 | 31 | 14-Facility rooms _by level | No |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-22 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-01 | Power Distribution | 8.71 | 50.95 | 48 | 14-Facility rooms _by level | No |  | yes (*) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) (13) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-21 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-02 | Corridor | 9.62 | 52.06 | 49 | 1474-Stairway | No |  | yes (*) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-03 | Corridor | 34.38 | 96.26 | 91 | 14-Facility rooms _by level | No |  | yes (*) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-25 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-04 | Room name IO restricted | 43.31 | 253.41 | 241 | 14-Facility rooms _by level | No |  | yes (*) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-53 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-05 | Corridor | 78.7 | 460.47 | 437 | 14-Facility rooms _by level | No |  | yes (*) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-26 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-06 | Corridor | 75.9 | 448.16 | 426 | 14-Facility rooms _by level | No |  | yes (*) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-26 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-07 | Corridor | 66.09 | 200.55 | 191 | 14-Facility rooms _by level | No |  | yes (*) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-27 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-08 | Corridor | 18.64 | 54.11 | 51 | 111474-Air-lock | No |  | yes (*) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-52 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-09 | Corridor | 14.08 | 82.39 | 78 | 1474-Stairway | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-10 | Power Distribution | 8.52 | 49.87 | 47 | 14-Facility rooms _by level | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) (13) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-22 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-11 | Ventilation Systems & Cubicles | 25.23 | 146.1 | 139 | 14-Facility rooms _by level | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-54 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5≤B≤6.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-12 | Corridor | 8.47 | 25.85 | 25 | 1474-Stairway | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-13 | Corridor | 9.8 | 27.44 | 26 | 1474-Stairway | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-20 | Room name IO restricted | 244.69 | 1452.3 | 1307.07 | 14-Process room on DS | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,2 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-11 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-02 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | 5 mT B≤ 15 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-B2-21 | Room name IO restricted | 33.88 | 198.28 | 178.452 | 14-Process room on DS | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 3,5 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-12 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-01 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤6 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-B2-22 | Room name IO restricted | 40.01 | 222.05 | 199.845 | 14-Process room on DS | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,2 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-11 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-02 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Orange | Orange | Orange | 0.15577 | 0.15577 |  | 5 mT B≤ 15 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-B2-23 | Room name IO restricted | 82.02 | 238.77 | 214.893 | 14-Facility rooms _by level | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-70 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | B≤ 19 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-24 | Room name IO restricted | 293.16 | 1646.27 | 1465.18 | 14-Process room on DS | No |  | yes (***) | yes (***) | Stainless Steel Liner |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,2 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-11 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-02 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | B≤ 19 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-B2-25 | Room name IO restricted | 220.78 | 1304.39 | 1043.512 | 14-Process room on DS | No |  | yes (***) | yes (***) | Stainless Steel Liner |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,2 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-11 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-02 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤ 12 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-B2-A1 | Airlock to Tokamak Building | 7.41 | 20.74 | 20 | 111474-Air-lock | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | No | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 14-FS-201 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Red | 0.15577 | 0.15577 |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-A2 | Airlock to Tritium Building | 6.08 | 17.03 | 16 | 111474-Air-lock | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-202 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-A3 | Airlock to Tritium Building | 10.97 | 33.46 | 32 | 111474-Air-lock | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-203 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-A4 | Airlock to Tokamak Building | 7.41 | 22.6 | 21 | 111474-Air-lock | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | No |  | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | No | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 14-FS-204 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 0.15577 | 0.15577 |  | 7 mT ≤B≤ 10 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-A5 | Airlock | 4.08 | 10.6 | TBD | 111474-Air-lock | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-50 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-205 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Green (if wall near the TKM lift is considered for shielding) | 0.15577 | 0.15577 |  | 7.5≤ B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-B2-F1 | Fire break zone | 6.52 | 22.82 | TBD | 111474-Air-lock | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | 4.1 for the external boundary of the volume comprising the FBZ and the process room | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) 1 for other walls | Yes | 1,2 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS but covered by 14-DS-12 | 1+1 (mutualization possible for global inlet and outlet ) | PIC/SIC-1 |  | Yes (metallic) | 14-FS-84 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-F2 | Fire break zone | 7.5 | 18.03 | TBD | 111474-Air-lock | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | 4.1 for the external boundary of the volume comprising the FBZ and the process room | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) 1 for other walls | Yes | 1,2 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS but covered by 14-DS-11 | 1+1 (mutualization possible for global inlet and outlet ) | PIC/SIC-1 |  | Yes (metallic) | 14-FS-85 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-F3 | Fire break zone | 2.67 | 5.88 | TBD | 111474-Air-lock | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | 4.1 for the external boundary of the volume comprising the FBZ and the process room | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) 1 for other walls | Yes | 1,2 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS but covered by 14-DS-11 | 1+1 (mutualization possible for global inlet and outlet ) | PIC/SIC-1 |  | Yes (metallic) | 14-FS-86 | PIC/SIC-1 | RE - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-F4 | Fire break zone | 6.31 | 22.08 | TBD | 111474-Air-lock | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | 4.1 for the external boundary of the volume comprising the FBZ and the process room | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) 1 for other walls | Yes | 3,5 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS but covered by 14-DS-50 | 1+1 (mutualization possible for global inlet and outlet ) | PIC/SIC-1 |  | Yes (metallic) | 14-FS-87 | PIC/SIC-1 | RE - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-L1 | North Personnel Lift Tokamak Building | 3.6 | 26.1 | 25 | 1474-Stairway | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-L2 | North Personnel Lift Tritium Building | 3.6 | 26.1 | 25 | 1474-Stairway | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-16 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-L3 | South Personnel Lift | 3.6 | 26.1 | 25 | 1474-Stairway | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5≤ B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-LFT | Large Lift | 24.29 | 195.57 | 186 | 111474-Air-lock (or process if rad materials transported) | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR (if no radioactive materials; otherwise, 4.1) (5) | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS (if no radioactive materials, otherwise DS sector) (5) | 1+1 ( if no radioactive materials otherwise 2+2 ) |  |  | Yes (metallic) | 14-FS-52 | PIC/SIC-2 if no radioactive materials (otherwise PIC/SIC 1 ) (5) | REI - 120 | PIC/SIC-2 if no radioactive materials (otherwise PIC/SIC 1 ) (5) | Manual extinction fix or not (9) | SR if no radioactive materials (otherwise PIC/SIC-2) (5) |  | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2M-01 | Room name IO restricted | 99.42 | 233.42 | 210 | 14-Process room on DS | No |  | yes (***) | yes (***) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) | 0, 1, 2 |  | 1 (for FS) | Yes | 1,2 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-11 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 14-FS-02 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤ 19 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-B2M-02 | Valve Room | 18.64 | 47.54 | 45 | 14-Facility rooms _by level | No |  | yes (***) | yes (***) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-66 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2M-V4 | Piping Shaft | 7.5 | 22.12 | 22 | 14-Process room on DS | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-51 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-23 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction ( room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤6 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-B2-S1 | North Stairway Tokamak Building | 17.52 | 102.53 | 97 | 1474-Stairway | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-S2 | North Stairway Tritium Building | 37.66 | 200.88 | 191 | 1474-Stairway | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-16 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-S3 | South Stairway Tokamak and Tritium Buidling | 17.67 | 103.36 | 98 | 1474-Stairway | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-SU1 | Sump | 78.53 | 459.42 | 436 | 14-Process room on DS | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,2 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-01 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 14-FS-28 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS | 1 | C2-HVACDS | 1 | C2-HVACDS | 1 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | B≤ 12 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-B2M-TG1 | North Tokamak Technical Gallery | 69.42 | 183.98 | 175 | 14-Facility rooms _by level (12) | No |  | yes (***) | yes (***) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-26 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2M-TG2 | North Tritium Technical Gallery | 101.03 | 242.47 | 242.47 | 14-Facility rooms _by level (12) | No |  | yes (***) | yes (***) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-26 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-V1 | Ventilation Systems Shaft | 18.08 | 91.96 | 87 | 14-Process room on DS | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-50 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-24 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Green | Green (if wall near the TKM lift is considered for shielding) | 0.15577 | 0.15577 |  | 5≤ B≤ 7.5mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-B2-V3 | Cable Tray Shaft | 6.24 | 36.5 | 35 | 14-Facility rooms _by level | No |  | yes (***) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-21 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-B2-V5 | Cable Tray Shaft | 6.18 | 36.19 | 34 | 14-Facility rooms _by level | No |  | yes (*) | yes (***) | Water tight lining, high chemical res. SIC Req, decontamination |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-22 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-01 | Power Distribution | 8.71 | 42.3558 | 40.238 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-21 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-02 | Corridor | 9.6285 | 45.764 | 43.4758 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No | / | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-03 | Corridor | 31.362 | 87.8136 | 83.4229 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-34 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-04 (nota 28) | SIC-2 train A cubicles Room | 43.318 | 208.5778 | 198.1489 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining and decontamination req, with specific conductive quality |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | Yes | -5000, +10000 | 0, 1, 2 |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-57 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-2 (7) |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-05 | Corridor | 96.2465 | 469.6829 | 446.1988 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-35 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-05A | Control & CODAC Cubicles | 74.7 | 358.4529 | 340.5303 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | N/A | 0, 1, 2 |  | No specified LR | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-75 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5≤B≤6.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-06 | Corridor | 75.9 | 370.392 | 351.8724 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-35 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-07 | Corridor | 36.6249 | 109.798 | 104.3081 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-36 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-07A | Control & CODAC Cubicles | 37.74 | 182.1132 | 173.0075 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | N/A | 0, 1, 2 |  | No specified LR | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-74 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-07E | Corridor | 34.98 | 106.689 | 106.689 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-36 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-08 | Corridor | 18.645 | 90.9876 | 86.4382 | 111474-Air-lock | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-306 (nota 26) | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-09 | Corridor | 14.084 | 68.7299 | 65.2934 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No | / | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-10 | Power Distribution | 8.525 | 41.602 | 39.5219 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) (13) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-22 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-11 | Ventilation Systems & Cubicles | 25.231 | 122.4973 | 116.3724 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-58 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5≤B≤6.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-12 | Corridor | 6.5 | 19.825 | 18.8337 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No | / | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-13 | Corridor | 9.802 | 27.4456 | 26.0733 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No | / | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-20 | Room name IO restricted | TBD | 127.1025 | 114 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) | 0, 1, 2 |  | 1 (for FS) | Yes | 1,2 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-11 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-02 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-L1-21 | Room name IO restricted | TBD | 336.2903 | 302.6613 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) | 0, 1, 2 |  | 1 (for FS) | Yes | 3,5 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-12 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-01 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5≤B≤6.5 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-L1-22 | Room name IO restricted | 344.045 | 1678.94 | 1511.046 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,75 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-19 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-11 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 1.56E-01 (TBC) | 1.56E-01 (TBC) |  | B≤16 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-L1-23 | Room name IO restricted | 223.65 | 1091.022 | 981.9198 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,5 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-20 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-12 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 1.56E-01 (TBC) | 1.56E-01 (TBC) |  | B≤16 mT | ZDN | Zone 2 | Be CZ | LPZ 1
14 | 14-L1-23A | Room name IO restricted | 24.45 | 119.316 | 107.3844 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) | 0, 1, 2 |  | 1 (for FS) | Yes | 1,5 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-20A | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-89 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 1.56E-01 (TBC) | 1.56E-01 (TBC) |  | B≤16 mT | ZDN | Zone 2 | Be CZ | LPZ 1
14 | 14-L1-23B | Room name IO restricted | 24.7 | 120.536 | 108.4824 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) | 0, 1, 2 |  | 1 (for FS) | Yes | 1,5 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-20B | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-90 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 1.56E-01 (TBC) | 1.56E-01 (TBC) |  | B≤16 mT | ZDN | Zone 2 | Be CZ | LPZ 1
14 | 14-L1-23C | Room name IO restricted | 26.8525 | 131.0402 | 117.9362 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) | 0, 1, 2 |  | 1 (for FS) | Yes | 1,5 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-20C | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-91 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 1.56E-01 (TBC) | 1.56E-01 (TBC) |  | B≤16 mT | ZDN | Zone 2 | Be CZ | LPZ 1
14 | 14-L1-24 | Room name IO restricted | 84.53 | 441.52 | 397.368 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | TBD | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-73 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | B≤12 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-L1-A1 | Airlock to Tokamak Building | 7.41 | 20.748 | 20 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | No |  | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | No | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-07 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 14-FS-301 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 499.2886 | 499.2886 |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | Be CZ | LPZ 1
14 | 14-L1-A2 | Airlock to Tritium Building | 6.084 | 17.0352 | 16.1834 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-302 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-A3 | Airlock to Tritium Building | 8.565 | 26.1232 | 24.8171 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-303 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-A4 | Airlock to Tokamak Building | 7.41 | 22.6 | 21 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 0,245 (for external walls global volume) (3) | No |  | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | No | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-07 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 14-FS-304 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 499.2886 | 499.2886 |  | 7 mT ≤B≤ 10 mT | ZDC | No zone | Be CZ | LPZ 1
14 | 14-L1-A5 | Airlock | 4.08 | 11.424 | TBD | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-50 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-305 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Green (if wall near the TKM lift is considered for shielding) | 499.2886 | 499.2886 |  | 7.5≤ B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-L1-F1 | Fire break zone | 11.28 | 55.0464 | TBD | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 for the external boundary of the volume comprising the FBZ and the process room 14-L1-21 4.1 for the external boundary of the volume comprising the FBZ and the process room 14-L1-22 | 0, 1, 2 | Yes | See column Q (LR in case of fire) | 0, 1, 2 |  | 1 | Yes | 3,5 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS but covered by 14-DS-12 and 14-DS-19 | 1+1 (mutualization possible for global inlet and outlet ) | PIC/SIC-1 |  | Yes (metallic) | 14-FS-96 (nota 26) | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤6.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-F2 | Fire break zone | 7.14 | 19.278 | TBD | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 for the external boundary of the volume comprising the FBZ and the process room 14-L1-23 4.1 for the external boundary of the volume comprising the FBZ and the process room 14-L1-24 | 0, 1, 2 | Yes | See column Q (LR in case of fire) | 0, 1, 2 |  | 1 | Yes | 1,5 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS but covered by 14-DS-20 and DS related to 14-L1-24 | 1+1 (mutualization possible for global inlet and outlet ) | PIC/SIC-1 |  | Yes (metallic) | 14-FS-93 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-F3 (nota 25) | Fire break zone | #N/A | #N/A | TBD | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) 1 for other walls | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-94 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-L1 | North Personnel Lift Tokamak Building | TBD | 19.368 | 18 | 1474-Stairway | No |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-L2 | North Personnel Lift Tritium Building | TBD | 19.368 | 18 | 1474-Stairway | Yes |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-16 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-L3 | South Personnel Lift | TBD | 19.368 | 18 | 1474-Stairway | No |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5≤ B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-LFT | Large Lift | TBD | 130.7071 | 124.1718 | 111474-Air-lock (or process if rad materials transported) | Yes |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR (if no radioactive materials; otherwise, 4.1) (5) | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS (if no radioactive materials, otherwise DS sector) (5) | 1+1 ( if no radioactive materials otherwise 2+2 ) | NA |  | Yes (metallic) | 14-FS-52 | PIC/SIC-2 if no radioactive materials (otherwise PIC/SIC 1 ) (5) | REI - 120 | PIC/SIC-2 if no radioactive materials (otherwise PIC/SIC 1 ) (5) | Manual extinction fix or not (9) | SR if no radioactive materials (otherwise PIC/SIC-2) (5) |  | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-S1 | North Stairway Tokamak Building | 17.5275 | 94.298 | 89.5831 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-S2 | North Stairway Tritium Building | 37.669 | 179.3056 | 170.3403 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-16 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-S3 | South Stairway Tokamak and Tritium Building | 17.67 | 95.0646 | 90.3114 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1M-TG1 | North Tokamak Technical Gallery | 65.459 | 116.5174 | 110.6915 | 14-Facility rooms _by level (12) | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-35 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1M-TG2 | North Tritium Technical Gallery | 103.705 | 158.6687 | 158.6687 | 14-Facility rooms _by level (12) | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-35 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-V1 | Ventilation Systems Shaft | 20.54 | 213.2357 | 202.5739 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-50 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-24 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Green | Green (if wall near the TKM lift is considered for shielding) | 499.2886 | 499.2886 |  | 7.5≤ B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-L1-V3 | Cable Tray Shaft | TBD | 33.5712 | 31.8926 | 14-Facility rooms _by level | Yes |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-21 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L1-V4 | Piping Shaft | TBD | 40.35 | 38 | 14-Process room on DS | No |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-51 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-23 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction ( room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤6 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-L1-V5 | Cable Tray Shaft | TBD | 33.28 | 32 | 14-Facility rooms _by level | Yes |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,13 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-22 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-01 | Power Distribution | 8.71 | 55.2214 | 52.4603 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-21 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-02 | Corridor | 9.6285 | 43.9559 | 41.7581 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-03 | Corridor | 37.535 | 105.098 | 99.8431 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-37 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-04 | Diagnostics Room | 43.318 | 274.3631 | 260.645 | 14-Facility rooms _by level | yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-59 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-05 | Corridor | 79.035 | 501.0819 | 476.0278 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-38 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-05A (nota 28) | SIC-1 train A cubicles Room | 40.46 | 254.2694 | 241.5559 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining and decontamination req, with specific conductive quality |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | No specified LR (14) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | Yes | -5000, +10000 | 0, 1, 2 |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-40 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-1 (7) |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤6.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-06 | Corridor | 75.9 | 481.206 | 457.1457 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-38 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-06A | Control & CODAC Cubicles | 32.7 | 111.78 | 106 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-76 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤6.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-07 | Corridor | 78.67 | 238.7735 | 226.8348 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-39 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-08 | Corridor | 18.645 | 118.2093 | 112.2988 | 111474-Air-lock | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-52 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-09 | Corridor | 7.904 | 50.1114 | 47.6058 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-10 | Power Distribution | 8.525 | 54.0485 | 51.3461 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) (13) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-22 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-11 | Ventilation Systems & Cubicles | 31.477 | 198.4092 | 188.4887 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-60 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5≤B≤6.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-12 | Corridor | 6.5 | 19.825 | 18.8337 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-13 | Corridor | 9.802 | 27.4456 | 26.0733 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-20 | Room name IO restricted | TBD | 166.212 | 149.5908 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) | 0, 1, 2 |  | 1 (for FS) | Yes | 1,2 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-11 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-02 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-L2-21 | Room name IO restricted | 392.1275 | 2599.023 | 2339.121 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-21 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-13 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | B≤16 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-L2-22 | Room name IO restricted | 52.345 | 329.2138 | 296.2924 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-22 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-14 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | B≤16 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-L2-23 | Room name IO restricted | 152.3319 | 974.6876 | 877.2188 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-45 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-77 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | B≤16 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-L2-24 | Room name IO restricted | 308.5175 | 1966.769 | 1770.092 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-32 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-15 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | B≤15 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-L2-A1 | Airlock to Tokamak Building | 7.41 | 20.748 | 20 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | No |  | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | No | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 14-FS-401 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 9.9858 | 9.9858 |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | Be CZ | LPZ 1
14 | 14-L2-A2 | Airlock to Tritium Building | 9.8674 | 27.6286 | 26 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-402 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-A3 | Airlock to Tritium Building | 8.565 | 26.1232 | 24.8171 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-403 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-A4 | Airlock to Tokamak Building | 7.41 | 22.6005 | 21 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | No |  | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | No | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 (16) |  | Yes (metallic) | 14-FS-404 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 9.9858 | 9.9858 |  | 7 mT ≤B≤ 10 mT | ZDC | No zone | Be CZ | LPZ 1
14 | 14-L2-A5 | Airlock | 3.12 | 8.736 | TBD | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-50 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-405 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Green (if wall near the TKM lift is considered for shielding) | 9.9858 | 9.9858 |  | 7.5≤ B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-L2-L1 | North Personnel Lift Tokamak Building | TBD | 18.648 | 18 | 1474-Stairway | No |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-L2 | North Personnel Lift Tritium Building | TBD | 18.648 | 18 | 1474-Stairway | Yes |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-16 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-L3 | South Personnel Lift | TBD | 24.624 | 23.3928 | 1474-Stairway | No |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5≤ B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-LFT | Large Lift | TBD | 166.1778 | 157.8689 | 111474-Air-lock (or process if rad materials transported) | Yes |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR (if no radioactive materials; otherwise, 4.1) (5) | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS (if no radioactive materials, otherwise DS sector) (5) | 1+1 ( if no radioactive materials otherwise 2+2 ) | NA |  | Yes (metallic) | 14-FS-52 | PIC/SIC-2 if no radioactive materials (otherwise PIC/SIC 1 ) (5) | REI - 120 | PIC/SIC-2 if no radioactive materials (otherwise PIC/SIC 1 ) (5) | Manual extinction fix or not (9) | SR if no radioactive materials (otherwise PIC/SIC-2) (5) |  | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-S1 | North Stairway Tokamak Building | 17.5275 | 90.7925 | 86.2528 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-S2 | North Stairway Tritium Building | 31.871 | 208.7444 | 198.3071 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-16 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-S3 | South Stairway Tokamak and Tritium Building | 17.67 | 120.8628 | 114.8197 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2M-TG1 | North Tokamak Technical Gallery | 69.145 | 192.8683 | 192.8683 | 14-Facility rooms _by level (12) | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-38 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2M-TG2 | North Tritium Technical Gallery | 103.705 | 310.0779 | 310.0779 | 14-Facility rooms _by level (12) | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-38 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-V1 | Ventilation Systems Shaft | 19.82 | 204.16 | 193.952 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-50 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-24 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Green | Green (if wall near the TKM lift is considered for shielding) | 9.9858 | 9.9858 |  | 7.5≤ B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-L2-V3 | Cable Tray Shaft | TBD | 42.6816 | 40.5475 | 14-Facility rooms _by level | Yes |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-21 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-V4 | Piping Shaft | TBD | 51.3 | 49 | 14-Process room on DS | No |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-51 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-23 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction ( room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤6 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-L2-V5 | Cable Tray Shaft | TBD | 42.3225 | 40.2064 | 14-Facility rooms _by level | Yes |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-22 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L2-V6 (nota 23) | RPD shaft | #N/A | #N/A | [81 empty] | 14-FS-98
14 | 14-L3-01 | Power Distribution | 8.71 | 55.65 | 73 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-21 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-02 | Corridor | 9.6285 | 74.42 | 82 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-03 | Corridor | 37.535 | 105.09 | 103 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-41 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-04 | Diagnostics Room | 43.318 | 276.59 | 275 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-61 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-05 | Corridor | 79.03 | 461.56 | 721 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-42 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-05A (nota 28) | SIC-1 train B cubicles Room | 38.64 | 223.12 | 232 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining and decontamination req, with specific conductive quality |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | N/A | 0, 1, 2 |  | No specified LR (14) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | Yes | -5000, +10000 | 0, 1, 2 |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-44 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-1 (7) |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-06 | Corridor | 103.12 | 602.25 | 850 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-42 (nota 26) | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-06A | Control & CODAC Cubicles | 32.7 | 111.78 | 101 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | N/A | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-78 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤6.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-07 | Corridor | 49.64 | 151.41 | 148 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-43 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-08 | Corridor | 18.65 | 119.14 | 117 | 111474-Air-lock | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-52 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-09 | Corridor | 7.9 | 50.5 | 111 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-10 | Power Distribution | 8.52 | 54.47 | 69 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) (13) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-22 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-11 | Ventilation Systems & Cubicles | 31.47 | 200.18 | 200 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-62 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5≤B≤6.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-12 | Corridor | 6.5 | 19.82 | 19 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-504 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-13 | Corridor | 9.8 | 27.44 | 14 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-20 | Room name IO restricted | 57.6 | 331.49 | 312 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) | 0, 1, 2 |  | 1 (for FS) | Yes | 1,2 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-11 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-02 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-L3-21 | Room name IO restricted | 350.52 | 2173.12 | 2140 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-22 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-14 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | B≤16 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-L3-22 | Room name IO restricted | TBD | 292.78 | 170 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | 14-DS-21 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-13 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (process & room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | B≤16 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-L3-23 | TCWS secondary cooling pipes | 473.69 | 2765.85 | 2664 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-17 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | 0.10929 | 0.10929 |  | B≤16 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-L3-A1 | Airlock to Tokamak Building | 7.41 | 20.74 | 20 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 0,245 (for external walls global volume) (3) | No |  | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 14-FS-501 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C3-DS | 0 | C3-HVACDS | 2 | C3-DS | 0 | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 117.5231 | 117.5231 |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-A2 | Airlock to Tritium Building | 9.73 | 27.26 | 28 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-502 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-A3 | Airlock to Tritium Building | 8.56 | 26.12 | 23 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-503 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-A4 | Airlock to Tokamak Building (South Est) | 7.41 | 22.6 | 21 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | 0,245 (for external walls global volume) (3) | No |  | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 14-FS-504 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C3-DS | 0 | C3-HVACDS | 2 | C3-DS | 0 | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 117.5231 | 117.5231 |  | 7 mT ≤B≤ 10 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-A5 | Airlock | TBD | #N/A | TBD | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-50 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-505 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Green | Green (if wall near the TKM lift is considered for shielding) | 117.5231 | 117.5231 |  | 7.5≤ B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-L3-F1 | Fire break zone | 12.68 | 43.76 | TBD | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 for the external boundary of the volume comprising the FBZ and the process room | 0, 1, 2 | Yes | See column Q (LR in case of fire) | 0, 1, 2 |  | 1 (for FS) | Yes | 1,2 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS but covered by 14-DS-11 | 1+1 (mutualization possible for global inlet and outlet ) | PIC/SIC-1 |  | Yes (metallic) | 14-FS-97 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤6.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-L1 | North Personnel Lift Tokamak Building | TBD | 30.78 | 29 | 1474-Stairway | No |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-L2 | North Personnel Lift Tritium Building | TBD | 30.78 | 29 | 1474-Stairway | Yes |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-16 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-L3 | South Personnel Lift | TBD | 24.8 | 28 | 1474-Stairway | No |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5≤ B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-LFT | Large Lift | TBD | 167.39 | 156 | 111474-Air-lock (or process if rad materials transported) | Yes |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR (if no radioactive materials; otherwise, 4.1) (5) | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS (if no radioactive materials, otherwise DS sector) (5) | 1+1 ( if no radioactive materials otherwise 2+2 ) | NA |  | Yes (metallic) | 14-FS-52 | PIC/SIC-2 if no radioactive materials (otherwise PIC/SIC 1 ) (5) | REI - 120 | PIC/SIC-2 if no radioactive materials (otherwise PIC/SIC 1 ) (5) | Manual extinction fix or not (9) | SR if no radioactive materials (otherwise PIC/SIC-2) (5) |  | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-S1 | North Stairway Tokamak Building | 12.88 | 136.49 | 145 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No | / | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-S2 | North Stairway Tritium Building | 30.82 | 199.22 | 251 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No | / | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-16 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-S3 | South Stairway Tokamak and Tritium Building | 16.62 | 109.67 | 146 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No | / | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3M-TG1 | North Technical Gallery | #REF! | 251.35 | 86 | 14-Facility rooms _by level (12) | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-42 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3M-TG2 | North Tritium Technical Gallery | #REF! | 221.88 | TBP | 14-Facility rooms _by level (12) | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-42 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-V1 | Ventilation Systems Shaft | 14.9 | 353.27 | 324 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-50 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-24 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Green | Green (if wall near the TKM lift is considered for shielding) | 117.5231 | 117.5231 |  | 7.5≤ B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-L3-V3 | Cable Tray Shaft | TBD | 42.99 | 53 | 14-Facility rooms _by level | Yes |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-21 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-V4 | Piping Shaft | TBD | 47.55 | 45 | 14-Process room on DS | No |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-51 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-23 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction ( room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤6 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-L3-V5 | Cable Tray Shaft | TBD | 42.63 | 50 | 14-Facility rooms _by level | Yes |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-22 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L3-V6 (nota 23) | RPD shaft | #N/A | #N/A | [81 empty] | 14-FS-98
14 | 14-L4-01 | Power Distribution | 8.71 | 61.4 | 64 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-21 (nota 26) | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-02 | Corridor | 9.05 | 63.73 | 73 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No | / | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-03 | Corridor | 24.38 | 74.37 | 70 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-45 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-04 | Control & CODAC Cubicles | 43.31 | 303.56 | 304 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-63 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-07 | Corridor | 34.96 | 106.64 | 95 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-69 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-08 | Corridor | 18.64 | 131.41 | 129 | 111474-Air-lock | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-52 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-09 | Corridor | 7.9 | 55.72 | 97 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No | / | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-10 | Power Distribution | 8.52 | 60.1 | 61 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) (13) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-22 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-11 | Ventilation Systems & Cubicles | 31.47 | 221.16 | 175 | 14-Facility rooms _by level | yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-64 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5≤B≤6.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-12 | Corridor | 5.62 | 17.15 | 15 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No | / | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-13 | Corridor | 13.79 | 42.08 | 24 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No | / | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-14 | Storage | 10.81 | 87.12 | TBD | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No | / | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-67 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-20 | Vault Annex (TBM Cooling System) | 490.29 | 3213.79 | 3053 | 1114-Vault | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | see TKM vault |  |  | 0.055 | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 | 0, 1, 2 (but HVAC not in work) | Yes (insulated) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 3348803.5534 | 3348803.5534 |  | B≤15 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-21 | Vault Annex (PHTS drainage and Drying System) | 372.08 | 2418.52 | 2298 | 1114-Vault | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | see TKM vault |  |  | 0.055 | yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 | 0, 1, 2 (but HVAC not in work) | Yes (insulated) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 3348803.5534 | 3348803.5534 |  | B≤15 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-22 | Vault Annex (Vault Coolers) | 215.4 | 1419.01 | 1354 | 1114-Vault | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | see TKM vault |  |  | 0.055 | yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  | Yes |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 | 0, 1, 2 (but HVAC not in work) | Yes (insulated) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 3348803.5534 | 3348803.5534 |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-23 | HVAC Filter Room | 146.64 | 953.16 | 906 | 1114-Vault | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | see TKM vault |  |  | 0.055 | yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 | 0, 1, 2 (but HVAC not in work) | Yes (insulated) | 11-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system | PIC/SIC-1 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 1 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 231 | 231 |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-A1 | Airlock to Tokamak Building Vault | 7.41 | 22.6 | 20 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0.055 (3) | No |  | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 14-FS-601 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 2 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 231 | 231 |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-A2 | Airlock to Tritium Building | 6.6 | 20.13 | 15 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-602 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-A3 | Airlock To Tritium Building | 7.51 | 22.92 | 21 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-603 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-A4 | Airlock to Tokamak Building Vault | 6.41 | 19.55 | 17 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0.055 (3) | No |  | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 14-FS-604 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 2 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 231 | 231 |  | B≤7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-A5 | Airlock | 3.12 | 8.74 | TBD | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-50 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-607 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Green | Green (if wall near the TKM lift is considered for shielding) | 117.5231 | 117.5231 |  | 7.5≤ B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-L4-A6 | Airlock to Vault Annex | 6.21 | 18.63 | 18 | 111474-Air-lock | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0.055 (3) | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 14-FS-605 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 2 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 231 | 231 |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-A7 | Airlock to Vault Annex | 6.48 | 19.44 | 18 | 111474-Air-lock | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0.055 (3) | Yes | 1,05 | No | [6 empty] | Yes | 100000 | 130 | 1 | 0 | No |  |  |  |  | Yes | 20000 | 130 | 0.44 | 0 | No |  |  |  |  | No | [6 empty] | Yes | 20000 | 125 | 0.44 | 0 1 (When HVAC is not in operation) | No |  |  |  |  | Yes | 20000 | 100 | 0.44 | 0, 1,2 (When HVAC is not in operation) |  |  |  | No |  |  |  | 11-DS-04 | 2+2 | PIC/SIC-1 |  | Yes (metallic) | 14-FS-606 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC2 |  | C3-DS | extrapolation 2E4KSJ | C3-HVACDS | 2 | C3-DS | extrapolation 2E4KSJ | yes |  | PIC/SIC-2 | 2 |  | Red | Yellow | Red | 231 | 231 |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-L1 | North Personnel Lift Tokamak Building | TBD | 27 | 26 | 1474-Stairway | No |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-L2 | North Personnel Lift Tritium Building | TBD | 27 | 26 | 1474-Stairway | Yes |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-16 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-L3 | South Personnel Lift | TBD | 27 | 26 | 1474-Stairway | No |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5≤ B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-LFT | Large Lift | TBD | 182.21 | 183 | 111474-Air-lock (or process if rad materials transported) | Yes |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR (if no radioactive materials; otherwise, 4.1) (5) | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS (if no radioactive materials, otherwise DS sector) (5) | 1+1 ( if no radioactive materials otherwise 2+2 ) |  |  | Yes (metallic) | 14-FS-52 | PIC/SIC-2 if no radioactive materials (otherwise PIC/SIC 1 ) (5) | REI - 120 | PIC/SIC-2 if no radioactive materials (otherwise PIC/SIC 1 ) (5) | Manual extinction fix or not (9) | SR if no radioactive materials (otherwise PIC/SIC-2) (5) |  | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-S1 | North Stairway Tokamak Building | 16.56 | 119.9 | 127 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-S2 | North Stairway Tritium Building | 16.83 | 120.71 | 220 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-16 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-S3 | South Stairway Tokamak and Tritium Building | 16.62 | 120.69 | 128 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4M-TG1 | North Technical Gallery | 54.89 | 203.09 | 203 | 14-Facility rooms _by level (12) | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-45 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4M-TG2 | South Technical Gallery | 57.19 | 211.54 | 212 | 14-Facility rooms _by level (12) | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-69 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-V1 | Ventilation Systems Shaft | 39.87 | 299.92 | 276 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-50 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-24 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Green | Green (if wall near the TKM lift is considered for shielding) | 231 | 231 |  | 7.5≤ B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-L4-V3 | Cable Tray Shaft | TBD | 43.99 | 46 | 14-Facility rooms _by level | Yes |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-21 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L4-V5 | Cable Tray Shaft | TBD | 43.57 | 44 | 14-Facility rooms _by level | Yes |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-22 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-01 | Power Distribution | TBD | TBD | 63 | 14-Facility rooms _by level | yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) (13) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-21 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-02 | Corridor | TBD | TBD | 49 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-03 | Corridor | TBD | TBD | 109 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-49 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-05 | Corridor | TBD | TBD | 787 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-50 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-05A | Control & CODAC Cubicles | TBD | TBD | 164 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) (roof) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-79 (nota 26) | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-06 | Corridor | TBD | TBD | 952 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-50 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-07 | Corridor | TBD | TBD | 129 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-51 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-08 | Corridor | TBD | TBD | 127 | 111474-Air-lock | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-52 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤7.55 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-09 | Corridor | TBD | TBD | 128 | 1474-Stairway | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-10 | Power Distribution | TBD | TBD | 59 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-22 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-11 | Ventilation Systems & cubicles | TBD | TBD | 172 | 14-Facility rooms _by level | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-65 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction and no water (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5≤B≤6.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-20 | Room name IO restricted | TBD | TBD | 2431 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [5 empty] | Yes |  | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (insulated) | 14-FS-19 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVAC (except if risk of bypass) | 2 | C2-HVAC (except if risk of bypass) | 2 | C2-HVAC (except if risk of bypass) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤7 mT | ZDN | Zone 2 | NA (no Be) | LPZ 1
14 | 14-L5-21 | Tokamak and Tritium Building HVAC exhaust filters&blowers | TBD | TBD | 4246 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (insulated) | 14-FS-20 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤7 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-L5-22 | Water tank room #1 | TBD | TBD | 143 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-47 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-23 | Water tank room #2 | TBD | TBD | 143 | 14-Facility rooms _by level | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-48 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-A2 | Airlock to Tritium Building | TBD | TBD | 34 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-702 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-A3 | Airlock to Tritium Building | TBD | TBD | 26 | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-703 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-A5 | Airlock | TBD | TBD | TBD | 111474-Air-lock | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (3) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-50 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-XX | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Green | Green (if wall near the TKM lift is considered for shielding) | 117.5231 | 117.5231 |  | 7.5≤ B≤ 5 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-L5-L1 | North Personnel Lift Tokamak Building | TBD | TBD | 25 | 1474-Stairway | No |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-L2 | North Personnel Lift Tritium Building | TBD | TBD | 25 | 1474-Stairway | Yes |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-16 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-L3 | South Personnel Lift | TBD | TBD | 25 | 1474-Stairway | No |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5≤ B≤ 6 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-LFT | Large Lift | TBD | TBD | 180 | 111474-Air-lock (or process if rad materials transported) | Yes |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR (if no radioactive materials; otherwise, 4.1) (5) | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS (if no radioactive materials, otherwise DS sector) (5) | 1+1 ( if no radioactive materials otherwise 2+2 ) |  |  | Yes (metallic) | 14-FS-52 | PIC/SIC-2 if no radioactive materials (otherwise PIC/SIC 1 ) (5) | REI - 120 | PIC/SIC-2 if no radioactive materials (otherwise PIC/SIC 1 ) (5) | Manual extinction fix or not (9) | SR if no radioactive materials (otherwise PIC/SIC-2) (5) |  | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-S1 | North Stairway Tokamak Building | TBD | TBD | 185 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-S2 | North Stairway Tritium Building | TBD | TBD | 215 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-16 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-S3 | South Stairway Tokamak and Tritium Building | TBD | TBD | 125 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | 5 mT ≤B≤ 7.5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5M-TG1 | North Technical Gallery | TBD | TBD | TBD | 14-Facility rooms _by level (19) | yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-50 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5M-TG2 | South Technical Gallery | TBD | TBD | TBD | 14-Facility rooms _by level (19) | yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-50 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-V1 | Ventilation Systems Shaft | TBD | TBD | 293 | 14-Process room on DS | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | 4.1 | 0, 1, 2 | Yes | 4,1 (for FS) 1 (globally for the buildings, concerns the external boundaries only) | 0, 1, 2 |  | 1 (for FS) 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | 14-DS-50 | 2+2 | PIC/SIC-1 |  | Yes (insulated) | 14-FS-24 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-1 |  | C2-HVACDS | 2 | C2-HVACDS | 2 | C2-HVACDS | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Green | Green (if wall near the TKM lift is considered for shielding) | 54.852 | 54.852 |  | B≤7.5 mT | ZDN | No zone | NA (no Be) | LPZ 1
14 | 14-L5-V3 | Cable Tray Shaft | TBD | TBD | 45 | 14-Facility rooms _by level | Yes |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-21 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-L5-V5 | Cable Tray Shaft | TBD | TBD | 43 | 14-Facility rooms _by level | Yes |  | No | yes (**) | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 0,245 (for external walls global volume) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | 1+1 (mutualization possible for global inlet and outlet ) |  |  | Yes (metallic) | 14-FS-22 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Fix automatic extinction (room) | PIC/SIC-2 |  | C2-HVAC | 2 | C2-HVAC | 2 | C2-HVAC | 2 | yes |  | PIC/SIC-2 | 1 |  | Green | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-R1-01 | Tokamak and Tritium Building HVAC Air Handling Unit | TBD | TBD | TBD | NA | No |  | yes (*) | No | Avoidance of water infiltration to the nuclear building |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | FZ - see ARFI Room Book | NA | see ARFI Room Book | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | NA | 0 | NA | 0 | NA | 0 | yes |  | NA |  |  | Red (forbiden access but requirement to add shielding) | Blue | Green | 9.9858 | 9.9858 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-R1-03 | Safety Related Chiller Unit | TBD | TBD | TBD | NA | (21) |  | yes (*) | No | Avoidance of water infiltration to the nuclear building |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | FS : different from 11-R1-01E (21) | Nota (21) | Nota (21) | PIC/SIC-1 | Extinction fix or not (9) | (17) |  | NA | 0 | NA | 0 | NA | 0 | NA |  | NA |  |  | Red (forbiden access but requirement to add shielding) | Blue | Green | 9.9858 | 9.9858 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-R1-04 | HVAC Room | TBD | TBD | 1612 | NA | No |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | FZ - see ARFI Room Book | NA | see ARFI Room Book | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C1 (6) | 2 | C1 (6) | 2 | C1 (6) | 2 | yes |  | NA |  |  | Red (forbiden access but requirement to add shielding) | Blue | Green | 9.9858 | 9.9858 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-R1-A1 | Airlock to Lift L1 | TBD | TBD | 29 | 1474-Stairway | Yes |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Blue | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-R1-A2 | Airlock to Tritium Building Roof | TBD | TBD | 28 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Blue | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-R1-A3 | Airlock to motor room | TBD | TBD | 15 | 111474-Air-lock | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes |  | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,05 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-803 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Fix automatic extinction (room) | PIC/SIC2 |  | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Blue | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-R1-L1 | Personnel Lift | TBD | TBD | 16 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Blue | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-R1-LFT | Large Lift (Machinery) | TBD | TBD | 84 | 111474-Air-lock (or process if rad materials transported) | Yes |  | yes (*) | No | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR (if no radioactive materials; otherwise, 4.1) (5) | 0, 1, 2 | Yes |  | 0, 1, 2 |  | 0,245 (for external walls global volume) (3) | Yes | 1,12 | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS (if no radioactive materials, otherwise DS sector) (5) | 1+1 ( if no radioactive materials otherwise 2+2 ) | NA |  | Yes (metallic) | 14-FS-52 | PIC/SIC-2 if no radioactive materials (otherwise PIC/SIC 1 ) (5) | REI - 120 | PIC/SIC-2 if no radioactive materials (otherwise PIC/SIC 1 ) (5) | Manual extinction fix or not (9) | SR if no radioactive materials (otherwise SIC2) (5) |  | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | C2-HVAC if no radioactive materials transported (otherwise C2-HVACDS) (5) | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Blue | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-R1-S1 | Stairway | TBD | TBD | 159 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-09 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Green | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
14 | 14-R1-S3 | Stairway | TBD | TBD | 104 | 1474-Stairway | Yes |  | yes (*) | yes (**) | Water tight lining, decontamination req |  | Yes | ±5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No | (14) |  |  | No specified LR (14) | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA (12) |  |  | Yes (metallic) | 14-FS-18 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | C2-HVAC(C1) | 2 | yes |  | PIC/SIC-2 | 1 |  | Red (forbiden access but requirement to add shielding) | Blue | Green | NA | NA |  | B≤5 mT | ZDC | No zone | NA (no Be) | LPZ 1
19 | 19-B2-01 | Seismic Basemat | TBD | TBD | TBD | N/A | No |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA |  |  | Yes (metallic) |  |  |  | PIC/SIC-2 | Manual extinction fix or not (9) | NA |  | NA | 0 | mobile ventilation | 0 | NA | 0 | N/A |  | NA | NA |  | White | White | White | NA | NA |  |  | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-01 | Control Cubicles Area North | 45.96 | 209.589 | 209.589 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-02 | Toilets | 16.32 | 74.442 | 74.442 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-03 | Cubicle Area for Diagnostics | 499.96 | 2279.555 | 2279.555 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-04 | Cubicle Area for Diagnostics | 626.94 | 2871.783 | 2871.783 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-07 | Microwave Laboratory | 77.76 | 354.6065 | 354.6065 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-09 | Divertor Impurity | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-10 | Cableway | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-11 | Dust Monitor | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-12 | Divertor Reflectometry, Spectrometers, Thomson Scattering | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-13 | Elevator Lobby | 17.35 | 79.135 | 79.135 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-14 | South Corridor Tokamak Building | 14.14 | 64.4784 | 64 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 |  |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-15 | Thomson Scattering | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-16 | Thomson Scattering I | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-17 | Thomson Scattering II | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-18 | Spectroscopy | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-20 | Spectroscopy I | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-22 | Electrical Laboratory | 28.86 | 131.6035 | 131.6035 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-24 | Cubicle & Electrical Distribution Room | 13.72 | 61.9562 | 61.9562 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-27 | South Corridor Diagnostic Building | 16.03 | 73.1025 | 73.1025 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-29 (nota 28) | SIC2 Cubicles Room | 28.1385 | 126.9685 | 127 | 74-PIC cubicles rooms | No* |  | yes (*) | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | Yes | ±5000 | 0, 1, 2 |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-04 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-2 (7) |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-ANW | North Airlock | 7.19 | 20.4915 | 20 | 111474-Air-lock | No* |  | yes (*) | yes (**) | Water tight lining, decontamiN/Ation req |  | Yes | +-5000 | Eurocode 2h | According to 2E4KSJ | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 1 (3) | No |  | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-05 | 2+2 but mutualization possible | PIC/SIC-2 |  | Yes (metallic) | 74-FS-201 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 3093.112 | 3093.112 |  | B≤ 7.5mT | ZDN | No zone | Be CZ | LPZ 1
74 | 74-B1-ASW | South Airlock | 7.35 | 20.9475 | 21 | 111474-Air-lock | No* |  | yes (*) | yes (**) | Water tight lining, decontamiN/Ation req |  | Yes | +-5000 | Eurocode 2h | According to 2E4KSJ | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 1 (3) | No |  | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-05 | 2+2 but mutualization possible | PIC/SIC-2 |  | Yes (metallic) | 74-FS-202 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 31.042 | 31.042 |  | 7.5 mT B≤ 12 mT | ZDN | No zone | Be CZ | LPZ 1
74 | 74-B1-LFT | Elevator (Lift) Area | TBD | 95.304 | 95.304 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-LS1 | South Lift for Tokamak Building | TBD | 17.955 | 18 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | According to 2E4KSJ | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | No | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | NA |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-LS2 | South Lift for Diagnostic Building | TBD | 17.955 | 17.955 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | 5≤B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-SN1 | North Stairway for Tokamak Building | 27.048 | 147.2367 | 145 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-01 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-SN2 | North Stairway for Diagnostic Building | 24.605 | 122.7178 | 122.7178 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-SS1 | South Stairway for Tokamak Building | 17.95 | 89.547 | 89.547 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-SS2 | South Stairway for Diagnostic Building | 17.95 | 89.547 | 90 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-VN1 | Cable Tray Shaf | TBD | 40.9545 | 40.9545 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-VN2 | HVAC Shaft North | TBD | 35.91 | 35.91 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-VN3 | Cable Tray Shaft | TBD | 18.791 | 18.791 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-VS4 | HVAC Shaft South | TBD | 109.972 | 109.972 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-VW1 | Busbar Shaft | TBD | 94.0595 | 94.0595 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-VW2 | Cable Tray Shaft | TBD | 21.1945 | 21.1945 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-VW3 | Cable Tray Shaft | TBD | 629.7066 | 629.7066 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-VW4 | Cable Tray Shaft | TBD | 16.3495 | 16.3495 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B1-VW5 | Busbar Shaft | TBD | 87.3905 | 87.3905 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-01 | Control Cubicles Area North | 69.37 | 385.757 | 385.757 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-02 | Technical Room | 10.47 | 58.691 | 58.691 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-03 | Switching Network and Fast Discharge for Lower Magnet System | 1142.89 | 6406.876 | 6406.876 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-06 | Elevator Lobby | 17.35 | 97.2705 | 97.2705 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-07 | Control Cubicles Area South | 77.76 | 431.908 | 431.908 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-08 | South Corridor Diagnostic Building | 16.03 | 44.1655 | 44.1655 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-10 | South Corridor Tokamak Building | 14.14 | 79.249 | 79 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 |  |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-11 | Cubicles + Electrical Distribution Room | 13.72 | 76.285 | 76.285 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-12 (nota 28) | SIC-2 Room | 28.52 | 158.061 | 158 | 74-PIC cubicles rooms | No* |  | yes (*) | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | Yes | ±5000 | 0, 1, 2 |  | No DS | NA |  |  | Yes (metallic) | 74-FS-02 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-2 (7) |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-ANW | Airlock to Tokamak bldg North | 7.19 | 20.4915 | 20 | 111474-Air-lock | No* |  | yes (***) | yes (***) | Water tight lining, decontamiN/Ation req |  | Yes | +-5000 | Eurocode 2h | According to 2E4KSJ | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 1 (3) | No |  | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | No | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 |  | Yes (metallic) | 74-FS-101 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Orange | 0.15731 | 0.15731 |  | B≤ 15mT | ZDN | No zone | Be CZ | LPZ 1
74 | 74-B2-ASW | Airlock to Tokamak bldg South | 7.35 | 20.9475 | 21 | 111474-Air-lock | No* |  | yes (***) | yes (***) | Water tight lining, decontamiN/Ation req |  | Yes | +-5000 | Eurocode 2h | According to 2E4KSJ | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 1 (3) | No |  | Yes | -6000 | 8000 | -15 | 40 | No specified LR | 0, 1, 2 | No | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-02 | 2+2 but mutualization possible | PIC/SIC-2 |  | Yes (metallic) | 74-FS-102 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Yellow | Orange | 0.15731 | 0.15731 |  | B≤ 15mT | ZDN | No zone | Be CZ | LPZ 1
74 | 74-B2-LFT | Elevator (Lift) Area | 19.11 | 147.0505 | 147.0505 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-LS1 | South Lift for Tokamak Building | 3.6 | 24.966 | 25 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA |  |  | No | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-LS2 | South Lift for Diagnostic Building | 3.6 | 24.966 | 24.966 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | 5≤B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-SN1 | North Stairway for Tokamak Building | 27.04 | 173.5745 | 174 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-01 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-SN2 | North Stairway for Diagnostic Building | 28.26 | 158.403 | 158.403 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-SS1 | South Stairway for Tokamak Building | 17.95 | 100.6335 | 101 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-SS2 | South Stairway for Diagnostic Building | 17.95 | 100.6335 | 100.6335 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-VN1 | Cable Tray Shaft North | 8.21 | 46.0275 | 46.0275 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-VN2 | HVAC Shaft North | 7.2 | 40.356 | 40.356 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-VN3 | Cable Tray Shaft North | 3.76 | 21.1185 | 21.1185 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-VS4 | HVAC Shaft South | 22.05 | 123.5855 | 123.5855 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-VW1 | Busbar Shaft North West | 18.85 | 105.7065 | 105.7065 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-VW2 | Cable Tray Shaft North West | 4.25 | 23.8165 | 23.8165 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-VW3 | Cable Tray Shaft West | 11.97 | 67.0985 | 67.0985 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-VW4 | Cable Tray Shaft South West | 3.27 | 18.373 | 18.373 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-B2-VW5 | Busbar Shaft South West | 17.52 | 98.211 | 98.211 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-01 | Control Cubicles Area North | 53.3687 | 249.6675 | 249.6675 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-02 | Toilet | 14.0835 | 65.9601 | 65.9601 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-03 | Cubicle Area for Diagnostics | 578.72 | 2709.202 | 2709.202 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-04 | Cubicle Area for Diagnostics | 572.5649 | 2652.753 | 2652.753 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-05 | North Corridor Diagnostic Building | 20.0875 | 94.11 | 94.11 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-06 | Control Cubicles Area South | 43.65 | 204.4348 | 204.4348 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-07 | Entry Access | 51.81 | 242.6521 | 242.6521 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-08 | Lidar I | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | 5 mT B≤ 10 mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-09 | Spectroscopy | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-10 | Spectroscopy I | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-11 | Electron Cyclotrom Emission | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-12 | Interferometer Polarimeter | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-13 | North Corridor Tokamak Building | 22.636 | 81.1363 | 81.1363 | 1474-Stairway | Yes |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-01 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | 2.5 mT B≤ 5 mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-14 | South Corridor Diagnostic Building | 16.1875 | 75.8142 | 75.8142 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-15 | Cableway | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-16 | Lidar | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-17 | Polarimeter | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-18 | Reflectrometer | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-19 | Spectroscopy | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-23 | South Corridor Tokamak Building | 14.14 | 66.2247 | 66 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-24 | Cubicle & Electrical Distribution Room | 13.72 | 63.6791 | 63.6791 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-25 (nota 28) | SIC 2 Cubicles Room | 18.8725 | 86.7944 | 87 | 74-PIC cubicles rooms | Yes |  | yes (*) | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | Yes | ±5000 | 0, 1, 2 |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-05 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-2 (7) |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-ANW | North Airlock | 7.192 | 20.4972 | 32 | 111474-Air-lock | Yes |  | yes (*) | yes (**) | Water tight lining, decontamiN/Ation req |  | Yes | +-5000 | Eurocode 2h | According to 2E4KSJ | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 1 (3) | No |  | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-07 | 2+2 but mutualization possible | PIC/SIC-2 |  | Yes (metallic) | 74-FS-301 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 3679.4905 | 3679.4905 |  | B≤ 15mT | ZDN | No zone | Be CZ | LPZ 1
74 | 74-L1-ASW | South Airlock | 7.35 | 20.9475 | 21 | 111474-Air-lock | Yes |  | yes (*) | yes (**) | Water tight lining, decontamiN/Ation req |  | Yes | +-5000 | Eurocode 2h | According to 2E4KSJ | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 1 (3) | No |  | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-07 | 2+2 but mutualization possible | PIC/SIC-2 |  | Yes (metallic) | 74-FS-302 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 25.8 | 25.8 |  | B≤ 15mT | ZDN | No zone | Be CZ | LPZ 1
74 | 74-L1-LFT | Elevator (Lift) Area | TBD | 97.6712 | 97.6712 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-LS1 | South Lift for Tokamak Building | TBD | 18.3996 | 18 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | No | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | NA |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-LS2 | South Lift for Diagnostic Building | TBD | 18.3996 | 18.3996 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | 5≤B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-SN1 | North Stairway for Tokamak Building | 20.358 | 104.0497 | 104 | 1474-Stairway | Yes |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-01 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-SN2 | North Stairway for Diagnostic Building | 17.255 | 88.1903 | 88.1903 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-SS1 | South Stairway for Tokamak Building | 17.955 | 88.4175 | 88.4175 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | No | 74-FS-03 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-SS2 | South Stairway for Diagnostic Building | 17.95 | 88.4175 | 88.4175 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-VN1 | Cable Tray Shaft | TBD | 41.9741 | 41.9741 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-VN2 | HVAC Shaft North | TBD | 36.7992 | 36.7992 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-VN3 | Cable Tray Shaft | TBD | 19.2648 | 19.2648 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-VS4 | HVAC Shaft South | TBD | 112.6975 | 112.6975 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-VW1 | Busbar Shaft | TBD | 96.3903 | 96.3903 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-VW2 | Cable Tray Shaft | TBD | 21.7218 | 21.7218 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-VW3 | Cable Tray Shaft | TBD | 61.1851 | 61.1851 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-VW4 | Cable Tray Shaft | TBD | 16.7577 | 16.7577 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L1-VW5 | Busbar Shaft | TBD | 89.5575 | 89.5575 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-01 | Control Cubicles Area North | 45.9637 | 204.6286 | 204.6286 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-02 | Toilet | 16.44 | 73.8731 | 73.8731 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-03 | Cubicle Area for Diagnostics | 655.6312 | 2944.49 | 2944.49 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-04 | Cubicle Area for Diagnostics | 476.4506 | 2152.37 | 2152.37 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-07 | Optical Laboratory | 78.215 | 351.3305 | 351.3305 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-08 | Diagnostic Cell Room | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-09 | Charge Exchange Resonance Spectrometry (CXRS), Diagnostic Neutral Beam (DNB), Core | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-11 | Neutron Diagnostic Area | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-12 | Main Reflectrometry | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-13 | Spectroscopy | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-14 | Divertor, Reflectrometry, Spectrometry, Thomson Scattering | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-15 | Main Reflectrometry | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-16 | Polarimetry | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-17 | H-Alpha Spectrometry | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-18 | Edge Thompson Scattering | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-19 | Spectrometry | TBD | TBD | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-21 | Instrumentation Laboratory | 28.9812 | 130.0986 | 130.0986 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-23 | North Corridor Diagnostic Building | 7.42 | 33.3418 | 33.3418 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-24 | North Corridor Tokamak Building | 6.27 | 38.9553 | 38.9553 | 1474-Stairway | Yes |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-01 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-25 | Elevator lobby | 17.355 | 77.9847 | 77.9847 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-26 | South Corridor Diagnostic Building | 16.1875 | 72.7385 | 72.7385 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-27 | South Corridor Tokamak Building | 14.14 | 63.5381 | 63.5381 | 1474-Stairway | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-30 | Cubicle & Electrical Distribution Room | 13.72 | 61.135 | 61.135 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-32 (nota 28) | SIC 2 cubicles room | 28.1185 | 124.6914 | 125 | 74-PIC cubicles rooms | Yes |  | yes (*) | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | Yes | ±5000 | 0, 1, 2 |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-06 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-2 (7) |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-ANW | North Airlock | 7.192 | 20.4972 | 20.4972 | 111474-Air-lock | Yes |  | yes (*) | yes (**) | Water tight lining, decontamiN/Ation req |  | Yes | +-5000 | Eurocode 2h | According to 2E4KSJ | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 1 (3) | No |  | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 |  | Yes (metallic) | 74-FS-401 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 764.1576 | 764.1576 |  | B≤ 15mT | ZDN | No zone | Be CZ | LPZ 1
74 | 74-L2-ASW | South Airlock | 7.35 | 20.9475 | 21 | 111474-Air-lock | Yes |  | yes (*) | yes (**) | Water tight lining, decontamiN/Ation req |  | Yes | +-5000 | Eurocode 2h | According to 2E4KSJ | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 1 (3) | No |  | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-08 | 2+2 but mutualization possible | PIC/SIC-2 |  | Yes (metallic) | 74-FS-402 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 58.4656 | 58.4656 |  | B≤ 15mT | ZDN | No zone | Be CZ | LPZ 1
74 | 74-L2-LFT | Elevator (Lift) Area | TBD | 94.0403 | 94.0403 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-LS1 | South Lift for Tokamak Building | TBD | 17.7156 | 18 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | No | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | NA |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-LS2 | South Lift for Diagnostic Building | TBD | 17.7156 | 17.7156 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | 5≤B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-SN1 | North Stairway for Tokamak Building | 20.358 | 100.1817 | 100 | 1474-Stairway | Yes |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-01 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-SN2 | North Stairway for Diagnostic Building | 17.255 | 84.9119 | 84.9119 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-SS1 | South Stairway for Tokamak Building | 17.955 | 88.3565 | 88 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | No | 74-FS-03 | PIC/SIC-2 | REI - 120 | SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-SS2 | South Stairway for Diagnostic Building | 17.955 | 88.3565 | 88.3565 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-VN1 | Cable Tray Shaft | TBD | 40.4137 | 40.4137 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-VN2 | HVAC Shaft North | TBD | 35.4312 | 35.4312 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-VN3 | Cable Tray Shaft | TBD | 18.546 | 18.546 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-VS4 | HVAC Shaft South | TBD | 108.508 | 108.508 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-VW1 | Busbar Shaft | TBD | 92.807 | 92.807 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-VW2 | Cable Tray Shaft | TBD | 20.9142 | 20.9142 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-VW3 | Cable Tray Shaft | TBD | 58.9105 | 58.9105 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-VW4 | Cable Tray Shaft | TBD | 16.1347 | 16.1347 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L2-VW5 | Busbar Shaft | TBD | 86.2282 | 86.2282 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-01 | Control Cubicles Area North | 85.32 | 519.51 | 497.382 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-02 | North Corridor Diagnostic Building | 7.42 | 45.55 | 43.2725 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-03 | Switching Network and Fast Discharges Upper Magnet System | 1148.26 | 7053.84 | 6786.477 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | 0.10929 | 0.10929 |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-04 | North Corridor Tokamak Building | 6.69 | 61.23 | 34 | 1474-Stairway | Yes |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-01 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-05 | Elevator lobby | 17.35 | 106.55 | 101.2225 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-06 | South Corridor Diagnostic Building | 16.18 | 99.39 | 94.4205 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-07 | Control Cubicles Area South | 78.21 | 477.02 | 464.626 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-09 | South Corridor Tokamak Building | 14.14 | 86.82 | 82 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-10 | Cubicles + Electrical Distribution Room | 13.72 | 83.62 | 80.028 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-11 (nota 28) | SIC-2 Room | 28.11 | 170.96 | 162 | 74-PIC cubicles rooms | Yes |  | yes (*) | yes (**) | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | Yes | ±5000 | 0, 1, 2 |  | No DS | NA |  |  | Yes (metallic) | 74-FS-07 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Automatic fire suppression system (7) | PIC SIC-2 (7) |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-ANW | Airlock To Tokamak bldg North | 7.19 | 23.73 | 40 | 111474-Air-lock | Yes |  | yes (*) | yes (**) | Water tight lining, decontamiN/Ation req |  | Yes | +-5000 | Eurocode 2h | According to 2E4KSJ | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 1 (3) | No |  | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | No | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-09 | 2+2 but mutualization possible | PIC/SIC-2 |  | Yes (metallic) | 74-FS-501 (nota 26) | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 117.5231 | 117.5231 |  | B≤ 15mT | ZDN | No zone | Be CZ | LPZ 1
74 | 74-L3-ASW | Airlock to Tokamak bldg South | 7.35 | 24.25 | 23 | 111474-Air-lock | Yes |  | yes (*) | yes (**) | Water tight lining, decontamiN/Ation req |  | Yes | +-5000 | Eurocode 2h | According to 2E4KSJ | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 1 (3) | No |  | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | No | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-09 | 2+2 but mutualization possible | PIC/SIC-2 |  | Yes (metallic) | 74-FS-502 (nota 26) | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | yes |  | PIC/SIC-2 | 1 |  | Red | Green | Red | 117.5231 | 117.5231 |  | B≤ 15mT | ZDN | No zone | Be CZ | LPZ 1
74 | 74-L3-LFT | Elevator (Lift) Area | TBD | 125.93 | 119.6335 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-LS1 | South Lift for Tokamak Building | TBD | 23.72 | 23 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | No | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | NA |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-LS2 | South Lift for Diagnostic Building | TBD | 23.72 | 22.534 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | 5≤B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-SN1 | North Stairway for Tokamak Building | 20.35 | 121.18 | 127 | 1474-Stairway | Yes |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-01 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-SN2 | North Stairway for Diagnostic Building | 17.25 | 104.02 | 108.0245 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-SS1 | South Stairway for Tokamak Building | 17.95 | 107.95 | 112 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-SS2 | South Stairway for Diagnostic Building | 17.95 | 107.95 | 112.404 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-VN1 | Cable Tray Shaft North | TBD | 54.12 | 51.414 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-VN2 | HVAC Shaft North | TBD | 47.44 | 45.068 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-VN3 | Cable Tray Shaft North | TBD | 24.83 | 23.5885 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-VS4 | HVAC Shaft South | TBD | 145.3 | 138.035 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-VW1 | Busbar Shaft North West | TBD | 124.28 | 118.066 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-VW2 | Cable Tray Shaft North West | TBD | 28 | 26.6 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-VW3 | Cable Tray Shaft West | TBD | 78.89 | 74.9455 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-VW4 | Cable Tray Shaft South West | TBD | 21.6 | 20.52 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L3-VW5 | Busbar Shaft South West | TBD | 115.47 | 109.6965 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L4-03 | South Corridor Diagnostic Building | 14.14 | 68.22 | 74.6795 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L4-29 | Ventilation room | 25.11 | 123.93 |  | N/A | Yes |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | No sepcified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-XX | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | NA |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L4-AN1 | Airlock Nort West | 5.58 | 26.95 | 28.4905 | NA | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | No | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L4-AN2 | Airlock North West 2 | 7.29 | 35.14 | 46 | NA | Yes |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | No | see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 15mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L4-LFT | Elevator (Lift) Area (Motor Room) | 19.11 | 106.2516 | 110.01 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | No | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | NA | NA | NA | NA | NA | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L4-LS1 | South Lift for Tokamak Building | TBD | 17.37 | 21 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | No | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | NA |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L4-LS2 | South Lift for Diagnostic Building | TBD | 17.37 | 20.7195 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | NA | NA | NA | NA | NA | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | 5≤B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L4-SN1 | North Stairway for Tokamak Building | 28.42 | 172.2252 | 160 | 1474-Stairway | Yes |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-01 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L4-SN2 | North Stairway for Diagnostic Building | 22.34 | 116.58 | 128.2785 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L4-SS1 | South Stairway for Tokamak Building | 17.95 | 86.6329 | 103 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L4-SS2 | South Stairway for Diagnostic Building | 17.95 | 86.6329 | 103.36 | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L4-VS4 | HVAC Shaft South | 22.05 | 133.623 | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L5-02 | South Corridor Tokamak Building | 14.14 | 51.47 | 49 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | 5 mT B≤ 10 mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L5-03 | Storage | 19.68 | 71.65 |  | N/A | yes |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-XX | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | NA |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | 2.5 mT B≤ 5 mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L5-AN1 | Airlock North West | 7.94 | 28.9 | 28 | NA | yes |  | No | No | Water tight lining, decontamiN/Ation req |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | No | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | NA |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | 2.5 mT B≤ 5 mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L5-ANW | Airlock to Tokamak bldg North | 7.19 | 26.17 | 25 | 111474-Air-lock | Yes |  | yes (*) | yes (**) | Water tight lining, decontamiN/Ation req |  | Yes | +-5000 | Eurocode 2h | According to 2E4KSJ | 0, 1, 2 | Yes | 1 (for external walls global volume) (13) | 0, 1, 2 |  | 1 (3) | No |  | Yes | -6000 | 8000 | 5 | 40 | No specified LR | 0, 1, 2 | Yes | 300 |  | 1 | 0 | No |  |  |  |  | No |  |  |  |  | Yes | 20000 | -170 (8) | No specified LR | 0, 1, 2 | No | [6 empty] | No |  |  |  |  | Yes | 20000 | 60 | 8.2 | 0, 1, 2 | No | [7 empty] | No |  |  |  | 11-DS-10 | 2+2 but mutualization possible | PIC/SIC-1 |  | Yes (metallic) | 74-FS-701 | PIC/SIC-1 | REI - 120 | PIC/SIC-1 | Manual extinction fix or not (9) | SR |  | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | C2-HVACDS or positive pressure | 1 | yes |  | PIC/SIC-2 | 2 (10) |  | Red | Blue | Blue | 0.11195 | 54.852 |  | B≤ 7.5mT | ZDN | No zone | Be CZ | LPZ 1
74 | 74-L5-LS1 | South Lift for Tokamak Building | TBD | 14.18 | 13 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | No | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 | Manual extinction fix or not (9) | NA |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L5-SN1 | North Stairway for Tokamak Building | 27.05 | 104.99 | 100 | 1474-Stairway | yes |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  | Yes (metallic) | 74-FS-01 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | PIC/SIC-2 | 1 |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-L5-SS1 | South Stairway for Tokamak Building | 17.95 | 68.55 | 67.203 | 1474-Stairway | No* |  | No | No | N/A |  | Yes | +-5000 | Eurocode 2h | No specified LR | 0, 1, 2 | No |  |  |  | No specified LR | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [11 empty] | No DS | NA | NA |  | yes (metallic) | 74-FS-03 | PIC/SIC-2 | REI - 120 | PIC/SIC-2 if PIC cable trays present on the room. Otherwise SR | Manual extinction fix or not (9) | SR |  | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | C2-HVAC(C1) | 1 | yes |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 7.5mT | ZDC | No zone | NA (no Be) | LPZ 1
74 | 74-R1-01 | Roof with VV PHTS Air Heat Exchangers, Safety Related Chillers Unit, Load Center, Cubicles, Ventilation Units | 10.66 | 24.52 | TBD | N/A | No* |  | No | No | N/A |  | No |  |  |  |  | No |  |  |  | NA | No |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No |  |  |  |  | No | [6 empty] | No |  |  |  |  | No |  |  |  |  | No | [7 empty] | No |  |  |  | No DS | NA | NA |  |  | FZ - see ARFI Room Book | NA | see ARFI Room Book |  | Manual extinction fix or not (9) | SR |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | NA | NA |  | Blue | Blue | Blue | NA | NA |  | B≤ 5mT | ZDC | No zone | NA (no Be) | LPZ 1