Table of Contents

1	Introduction	2

1.1	Scope	2

1.2	Background and Objectives	2

1.3	Definitions and Abbreviations	2

2	Description of the FE Analysis	3

2.1	Software Package	3

2.2	Units	3

2.3	Coordinate System(s)	3

2.4	Analyses Inputs	3

2.4.1	Input Excitations	3

2.4.2	Input geometry	4

2.5	The EM Models	4

2.5.1	Evaluation of 2D equivalent resistivities for vessel and cryostat	5

2.5.2	The Axis-symmetric model of the building	5

2.5.3	The axis-symmetric model for stray field inside the bioshield	5

2.5.4	Material properties	5

2.5.5	Mesh characteristic	7

2.5.6	Boundary conditions	7

3	Results of the analyses	7

3.1	Stray field mapping data	8

4	Comparison with previous work and RPrS field maps	9

5	Effect of PFC fast discharge on stray field time derivative in tokamak complex	10

5.1	Analysis cases including the PFC fast discharge	10

5.2	Results of PFC-FD analysis	12

Results of these analyses are summarised in figures 5.2 to 5.6, in particular:	12

6	Conclusions	12

7	References	13

8	Figures	14

# Introduction

## Scope

The activity is aimed to provide the worst working operational conditions in terms of stray field and of stray field time derivative maxima in the ITER tokamak complex where these quantities can achieve not negligible values. To this end the evaluation of stray field and its time derivative in a wide region including the tokamak building has been performed during normal and off-normal (plasma disruption) operation scenarios.

## Background and Objectives

The maximum Bdot, and thus the maximum of eddy currents and EM loads induced in the conducting structures located inside the TKM building, are expected to occur during plasma disruptions or during the plasma normal operation (at plasma initiation or at plasma end).

Due to the relative high distance from the vessel and the large time constants of vessel and cryostat, the EM transient outside the bio-shield is quite independent on the disruption type: if driven by a downward or upward VDE or if due to a MD. This fact has been checked in the previous version (1.1) of the work [1]. Due to this fact only two fast disruptions have been analysed the VDE Fast Down linear Current Quench of 36 ms (15MA VDE _FD_lin36ms) starting from the SOB of a 15MA plasma and the Main Disruption 41ms linear Current Quench starting from the SOB of a 17MA plasma (17MA MD_lin41ms). The effect on Bdot of eddy currents induced in the building structures due to the presence of concrete reinforcement has been taken into account; the assumed value for the concrete conductivity [2] can be reasonably considered an upper limit. The Bdot has been also evaluated considering the concrete of building made of non-conductive material. It has been found that in this case it was somehow lower than the value found in presence of eddy currents in the conducting structures. Furthermore the magnetic field time derivative during plasma disruptions was found much higher than the maximum Bdot reached during the normal operating scenario and also higher than in case of PF coils fast discharge (as discussed in section 5).

The field time derivative inside the bio-shield is, on the other hand, more directly dependent on the type of plasma disruption, for this reason three different cases have been analysed (as explained in section 2.5.3)

In case of plasma disruptions the stray field reaches its maximum some seconds after the plasma current quenches (when even the eddy currents in the conducting structures are lowered practically to zero). Indeed the plasma current tends to compensate the field produced by the PFC. Thus, since the stray field is higher in absence of plasma and the eddy currents decay in times much shorter (some seconds) than the time needed to low down the PFC currents, the maximum of stray field during a disruption depends strongly on the time of the scenario at which the disruption occurs. In practice, this is equal to the field produced by the PFC only, at the disruption time. To find the absolute maximum of stray field in any situation is then enough to find the stray field maximum during the full operational scenario in absence of plasma.

## Definitions and Abbreviations

The main abbreviations used in the text are listed below:

- SOB : start of burn;

- SOD : start of discharge;

- VDE: vertical displacement event

- MD: Major disruption

- EOP: Endo of plasma;

- CQ: current quench;

- TQ: thermal quench;

- CS: Central solenoid;

- PFC: poloidal field coils;

- SOB_15MA_DE _FD_lin36ms: Fast Down VDE of type III with linear CQ of 36 ms duration  starting from SOB of 15 MA plasma scenario (PFC scenario at disruption beginning taken from 15 MA full operational scenario[3] - about 75s after SOD) ;

- SOB_17MA_MD_lin41ms: MD with linear CQ of 41 ms duration  starting from SOB of 17 MA plasma scenario (PFC scenario at disruption beginning taken from 17 MA full operational scenario[4] - about 154s after SOD) ;

- VV: Vacuum vessel.

# Description of the FE Analysis

## Software Package

The software used for the EM analysis was The ANSYS code (Mechanical APDL version 12.1). The ANSYS FE Element used was the axis 8 nodes symmetric element Plane53 and two DOF per each node the z component of potential vector Az and the volt V.

## Units

The SI has been used for all the units.

## Coordinate System(s)

The coordinate reference frame is the ITER global reference frame with the Z axis oriented upward in vertical direction and the X axis in radial direction (see the note in the next section).

## Analyses Inputs

### Input Excitations

For the plasma disruptions the DINA simulation outputs have been used as inputs for the EM analyses.

The PFC scenarios of the DINA outputs have been corrected by the difference between the PFC currents at Start Of Burn (SOB), as it is assumed in the starting configuration of equilibrium in the version of DINA code used for the numerical simulation of plasma disruption, and the PFC currents at SOB obtained by the version of DINA used for the simulation of the normal operational scenarios.

This difference while quite ineffective on the field in the plasma region and thus on the plasma equilibrium and on the plasma evolution during the disruption has not negligible effects on the correct evaluation of the stray field at large distances from the tokamak. For this purpose it is important that the poloidal coil currents are the real PFC currents at SOB during the normal operational scenario.

The DINA outputs for the plasma are given in form of filament arrays whose current and position varies during the simulations. Since the use of moving conductors is out of the possibility of ANSYS, an interface has been used (the EMAG code [5]) to transfer the original DINA excitations to equivalent excitations to be used in the ANSYS code. In practice using this interface the original DINA outputs have been reduced to a new array of equivalent secondary excitations whose position is fixed in time. The full equivalence of secondary and primary excitation has been demonstrated in ref.[5].

The four following cases have been considered for assessment of field and field time derivative in the tokamak complex in the region outside the bio-shield:

- Full operational scenario at 15 MA[3];

- VDE at 15 MA 36 ms lin. CQ[6], starting from SOB of scenario1);

- Full operational scenario at 17 MA[4];

- MD at 17 MA 41 ms lin. CQ[7], starting from SOB of scenario3);

The plasma and PFC currents vs. time of these scenarios are given in the figures 2.1 to 2.12.

For the assessment of the maximum field and field time derivative inside the bio-shield the following three disruptions have been taken into account:

1) Fast Upward VDE with 36 ms linear current quench (category III);

2) Fast Downward VDE with 36 ms linear current quench (category III);

3) Upward Major Disruption with 16 ms exponential current quench (category II).

Note: In these figures the sign of currents is coherent with the convention of DINA code, where the verse of plasma current is assumed as positive. In reality in a cylindrical coordinate system that has the vertical axis upward, like in the ITER building reference frame, the plasma current and thus the currents in all poloidal coils must be reversed in sign (in the tokamak reference frame the ITER plasma is indeed clockwise). The stray field of the tables is coherent with the assumption of a vertical axis upward and then with a negative sign for the plasma current.

### Input geometry

The geometry and the material properties used for the VV and the cryostat are the same used in reference[1].  The effect of the main 3-D features (like openings, ribs, and so on) on the time constants of vessel and cryostat have been evaluated using a 3-D model[1and 8]. Doing in this way it has been possible to approximate these components with 2D axis-symmetric equivalent models (see below).

The geometry of the building[9]  is shown in the figures 2.13 and 2.14.

## The EM Models

The axis-symmetric approximation of the building and of the main conducting structures inside the building has been performed following the guide line described below:

a) Axis-symmetric approximation of vessel and Cryostat:

b) Axis symmetric approximation of building floors and roofs:

The roofs and floors have been approximated by disks of finite thickness whose conductance is half of total Fe conductance in the concrete. Since the stray field is, for the most poloidal, eddy currents flow only in the Fe bars that can link a net poloidal flux variation. Since the  local loops, due to their short range effect, can be neglected, it has been supposed that only half of the Fe bars in the concrete could have some significant effect on the stray field;

c)  Axis symmetric approximation of building walls:

Only the building walls of TKM room have been considered (see 2.13). The rectangular shape of TKM room has been approximated to a cylinder of equal cross section and equal thickness in order to have approximately the same self-inductance of real rectangular wall box. The equivalent resistivity of the cylindrical wall was such to obtain a resistance equal to the resistance of the real rectangular box with an equal Fe content.

### Evaluation of 2D equivalent resistivities for vessel and cryostat

The equivalent resistivities of VV and cryostat have been evaluated in ref. [1]. And are summarized in the table of chapter 2.5.3

### The Axis-symmetric model of the building

The horizontal cross section at level2, and the vertical cross section (view from west) at position A-A of the horizontal cross section are shown in the figs fig 2.13 and 2.14. Only the part of building included in the coloured frame has been modelled. The most external walls included in the rectangle that are of rectangular shape in the model have been approximated by a cylinder of equal thickness and cross section.

The conducting parts of the axis symmetric model used for the evaluation of stray field are shown in fig. 2.15. A particulars of the model showing the axis symmetric model of the vessel of the cryostat and of excitations is shown in fig. 2.16.

Respect to the model of the previous work[1] the actual FEM has been extended in such a way to have a quite precise map of field up to a radial distance from the tokamak axis of 120 m (the previous was up to 60 m) and up to a height of 60 m ( the previous was up to 16 m). In the figure 2.18 the building region mapped by this and by the model of previous work is shown.

### The axis-symmetric model for stray field inside the bioshield

For these analyses the model has been changed as shown in Fig 2.17 in order to have a much more refined mesh in the region inside the bioshield. The effect of building in this region is negligible and has not been taken into account. This fact allowed an important simplification of the mesh outside the bioshield.

For the analyses related to the region inside the bioshield, only plasma disruptions have been analyzed. Since the region inside the bioshield is very close to the source of EM transient, the values of stray field strongly depend on the type of plasma disruption. For this reason two fast VDE (fast upward with 36 ms lcq and fast downward with 36 ms lcq) and one fast MD (upward major disruption with 16 ms ecq) have been analyzed for this case.

The values of field and field time derivative have been calculated by means of a 2D axisymmetric model. The static stray field can be, with good approximation, considered axisymmetric and, thus, well reproduced by these calculation. The field time derivative should be, instead, considered valid only externally to the port extensions.

The toroidal field inside the bioshield has also been evaluated by means of a 3D model where the TFC have been modelled in detail. Due to the relevant distance in toroidal direction between two adjacent TF coils (in particular at the equatorial level) the stray toroidal field is not negligible. The maps reported show the two main components of the toroidal field (radial and toroidal) and its modulus on the equatorial plane (where the ripple and thus the stray toroidal field reach their maxima).

### Material properties

The resistivities of 3D models of vessel and cryostat are taken from ref. [6]. The Fe content in the various concrete structures is taken from ref. [8]. For the Fe of concrete reinforcement has been assumed the resistivity at room temperature of SS316LN that is one of the most used material for concrete reinforcement. The averaged resistivity of each concrete component used in the model can be calculated from the table of material properties by the formula below; the meaning of symbols used in the formula are given in the table

Table of Material Properties

| Component | Resistivity ρ of conducting material | Fraction P of conducting material in the component | Fraction Q of conducting material effective |
| --- | --- | --- | --- |
| 3-D vessel | 0.8 E-7 | 1.00 | 1.00 |
| 3-D cryostat | 0.71E-7 | 1.00 | 1.00 |
| 2-D vessel | 0.79E-6 | 1.00 | 1.00 |
| 2-D cryostat | 0.83E-6 | 1.00 | 1.00 |
| Bioshield | 0.72E-6 | 0.045 | .50 |
| Basemat | 0.72E-6 | 0.03 | .50 |
| Building walls | 0.72E-6 | 0.04 | .50 |
| Roof of Vessel room | 0.72E-6 | 0.04 | .50 |
| Floors 1 to 4 | 0.72E-6 | 0.025 | .50 |

### Mesh characteristic

The element name type and their approximate number in the mesh of the 3D and 2D ANSYS FEM models used for the analyse is given in the table below

FE mesh: element type and number[8]

| Element Type | Nodes | Name | DOF number per node | Used for conducting element | Used for non conducting element | Number of element in the model |
| --- | --- | --- | --- | --- | --- | --- |
| 2-D Plane | 8 | Plane53 | 2 | yes | no | ̴ 10000 |
| 2-D Plane | 8 | Plane53 | 1 | no | yes | ̴ 100000 |
| 2-D Plane | 8 | Infinit110 | 1 | no | yes | ̴ 300 |

### Boundary conditions

In the 3-D models the boundary conditions were: tangent field at the nodes of boundary poloidal planes at 0 and 20°; V=0 at the nodes of conducting elements of the boundary planes that have toroidal continuity through these planes; INFINIT surface flag at the external nodes of the element INFINIT 111; Null value for all three component of potential vector at the node on the axis.

For the 2D models the boundary conditions were; V=0 at the nodes of conducting elements of the boundary planes that have toroidal continuity through these planes; Infinite surface flag at the external nodes of the element INFINIT110; Null potential vector at the node on the axis.

# Results of the analyses

The stray field and its time derivative outside the bio-shield has been analysed both for 15 and 17 MA plasmas in presence of plasma disruptions and during the normal operating scenarios. To find the worst operating conditions all the cases listed below have been analysed:

- Case1: Vertical Displacement Event (VDE) linear of 36 ms Current Quench (CQ) duration; starting from the PFC current distribution at SOB of the 15 MA normal operating scenario; In this case the building walls and floors are conducting(see below);

- Case2: Same of case 1 except for the building that is non-conducting;

- Case3: Normal operating scenario at 15 MA (conducting building);

- Case4: Normal operating scenario at 15 MA (building non-conducting);

- Case5: Normal operating scenario at 15 MA with plasma off (conducting building);

- Case6: Normal operating scenario at 15 MA with plasma off (building non-conducting);

- Case7: Main Disruption (MD) linear of 41 ms Current Quench (CQ) duration; starting from the PFC current distribution at SOB of the 17 MA normal operating scenario; In this case the building walls and floors are conducting(see below);

- Case8: Same of case 1 except for the building that is non-conducting;

- Case9: Normal operating scenario (conducting building);

- Case10: Normal operating scenario at 17 MA (building non-conducting);

- Case11: Normal operating scenario at 17 MA with plasma off (conducting building);

- Case12: Normal operating scenario at 17 MA with plasma off (building non-conducting).

In the figure from 3.1 to 3.12 |B| and d|B|/dt are plotted vs. time at equatorial level and from for six distances from tokamak axis in steps of 5m starting from a distance of 17 m – that is just outside the bio-shield. From these figures it is apparent what follows:

- The d|B|/dt is much higher during the disruptions than during the normal operating scenarios;

- The d|B|/dt is slightly higher when the building concrete is conductor than when it is insulated;

- The maximum |B| reached during the full scenarios without plasma are higher than the maximum field reached in the correspondent scenarios with the plasma included;

- The maximum |B| reached during a full scenario is higher of than the maximum |B| reached after a plasma disruption starting from SOB of this scenario;

- During a normal operating scenario, due to the very slow time dependence of the currents in the plasma and in the PFC the stray field is in practice independent on the electrical properties of the conducting materials in the building.

As a consequence of these facts only two cases should be considered: 1) the disruption in presence of conducting building for the search of dBxdt, dBzdt and of d|B|/dt maximum; 2) the full scenario without plasma for the search of maximum of Bx, By and of |B|. In any case, even the field and its time derivative are obviously higher for a 17 MA than for a 15 MA plasma, due to the fact that the normal working conditions are, by far, much more related to a 15 MA than to a 17 MA plasma, the maxima of these quantities have been mapped for both 15 and 17 MA plasmas.

The figures 3.13 to 3.24 show the poloidal field and field time derivative in the region between the VV and the bioshield during: Fast Downward VDE III with 36 ms linear current quench (fig. 3.13 -3.16); Major Disruption II with 16 ms exponential current quench (fig. 3.17 – 3.20) and Fast Upward VDE III with 36 ms linear current quench (fig. 3.12 – 3.24).

The toroidal field inside the bio-shield is shown in figures 3.25 – 3.27.

## Stray field mapping data

For the four scenarios of case1, case5, case7 and case11 in which the maxima of stray field and of field time derivative occur a more accurate analysis has been performed. The Building Region (BR) (x from 0 and 120 m) and ( z from -13 to 60 m), with exclusion of the tokamak region: (x from 0, to 15 m) and (z from -12 m to 17 m), has been subdivided in about 300 x 150 cells. For each cell the maximum of stray field and field time derivative modulus and of radial and vertical components occurring in its centre during the event has been found and tabulated together with the position of the cell centre and the time at which the maximum occurs. The cell centres are stepped by about 0.5 m both in x and in z direction.

These data are reported in the four following files:

- Bdot_VDE_15MA36ms_from_SOB_BLDYES.dat: the absolute maxima of dBx/dt, dBz/dt and of d|B|/dt produced in any given position inside the BR by any 15MA plasma can be obtained interpolating the data of this file;

- B_FULL_SCEN_15MA_PLANO__BLDYES.dat: the absolute maxima of Bx, Bz and of |B| produced in any given position inside the BR by any 15MA plasma can be obtained interpolating the data of this file;

- Bdot_MD_17MA41ms_from_SOB_BLDYES.dat: the absolute maxima of dBx/dt, dBz/dt and of d|B|/dt produced in any given position inside the BR by any 17MA plasma can be obtained interpolating the data of this file;

- B_FULL_SCEN17MA_PLANO__BLDYES.dat: the absolute maxima of Bx, Bz and of |B| produced in any given position inside the BR by any 17MA plasma can be obtained interpolating the data of this file;

These files in form text and excel files are in IDM attached to this report.

# Comparison with previous work and RPrS field maps

The field maps have been produced basing on the updated reference 17 MA scenario [4]. This is slightly different from the scenario used for the analyses reported in a previous work [10]: which was used as basis for the Preliminary Safety Report [11]. Table 4.1 reports the maximum magnetic moments during the older scenario while table 4.2 shows the maximum magnetic moments for the scenario [4] used for the present document. The new scenario implies, in general, slightly higher stray field values. Figures 4.1 to 4.3 show the increase of stray field at the level (B1) where it reaches its maximum during the above mentioned scenario. Especially important is the 10 mT limit which defines the boundary of the non-controlled zone as specified in the RPrS document (Chapter 9.5: Magnetic Zoning). The figures demonstrate that none of the building surrounding the tokamak will need to change zoning due to the new updated maps.

Building 14 and 74 (fig. 4.1) were already in the controlled zone as well as building 13 (fig. 4.2). Building 21 (Hot-Cell) was outside the controlled zone and also with the updated scenario remains (even though marginally) outside of the 10 mT limit (top left in fig. 4.3). The 200 mT limit which is the boundary of the prohibited zone also moves slightly outward with the updated scenario as shown by the comparison of figure 4.4. Figure 4.5 shows that the 200 mT curve exceeds the bioshield concrete wall of less than half meter at level L1-L2. Anyway when the PF and CS coils are energized port cells and galleries are already classified as prohibited zones. In conclusion the updated maps reported in this document do not entail any change in the reference magnetic zoning reported in [11].

Table 4.1 – Maximum magnetic moments during 17 MA scenario used in [10]

| Coil | turns | nI [MA-turn] | I [kA] | M [mp-m^2] |
| --- | --- | --- | --- | --- |
| PF1 | 249 | 2.76 | 11.1 | 1.35E+08 |
| PF2 | 106 | -0.66 | -6.2 | -1.43E+08 |
| PF3 | 185 | -6.86 | -37.1 | -3.10E+09 |
| PF4 | 169 | -5.14 | -30.4 | -2.31E+09 |
| PF5 | 217 | -7.27 | -33.5 | -1.61E+09 |
| PF6 | 425 | 18.59 | 43.7 | 1.06E+09 |
| CS3U | 548 | -1.14 | -2.1 | -1.06E+07 |
| CS2U | 548 | -15.58 | -28.4 | -1.45E+08 |
| CS1U | 548 | -21.08 | -38.5 | -1.96E+08 |
| CS1L | 548 | -21.67 | -39.5 | -2.02E+08 |
| CS2L | 548 | -16.43 | -30 | -1.53E+08 |
| CS3L | 548 | 0.42 | 0.8 | 3.91E+06 |
|  |  |  | Total Magnetic Moment [mp-m^2] | -6.67E+09 |

Table 4.2 – Maximum magnetic moments from 17 MA scenario used for present work [4]

| Coil | turns | nI [MA-turn] | I [kA] | M [mp-m^2] |
| --- | --- | --- | --- | --- |
| PF1 | 249 | 3.987984 | 16.016 | 1.95E+08 |
| PF2 | 106 | -1.080034 | -10.189 | -2.35E+08 |
| PF3 | 185 | -8.202345 | -44.337 | -3.71E+09 |
| PF4 | 169 | -3.795909 | -22.461 | -1.71E+09 |
| PF5 | 217 | -10.498026 | -48.378 | -2.32E+09 |
| PF6 | 425 | 16.9405 | 39.86 | 9.67E+08 |
| CS3U | 548 | -4.0548164 | -7.3993 | -3.78E+07 |
| CS2U | 548 | -19.761428 | -36.061 | -1.84E+08 |
| CS1U | 548 | -24.516424 | -44.738 | -2.28E+08 |
| CS1L | 548 | -24.516424 | -44.738 | -2.28E+08 |
| CS2L | 548 | -19.844724 | -36.213 | -1.85E+08 |
| CS3L | 548 | 3.266354 | 5.9605 | 3.04E+07 |
|  |  |  | Total Magnetic Moment [mp-m^2] | -7.68E+09 |

# Effect of PFC fast discharge on stray field time derivative in tokamak complex

The study of the poloidal field coils fast discharge has been also included in the analyses to make sure that the maximum stray field time derivative presented in the maps corresponds to the actual worst case. The analysis results show that the MD with fixed current in the PFC and CS coils, used as basis for the preparation of the PF maps described in this document, produces higher level of B_dot than the FD of the PF and CS coils.

## Analysis cases including the PFC fast discharge

Four different cases have been analysed and compared:

- Case A: 17 MA plasma MD 41 ms Linear. MD starting at SOB; PFCs with imposed current assumed constant after plasma Current Quench End (CQE) (induced current allowed on all passive conductors but not allowed on PFCs). This is the case documented in detail in this document;

- Case B: 17 MA plasma MD; Induced currents are allowed in PF and CS coils. These are simulated by stranded coils closed on their true operational resistances (shown in table 5.1) and fed by constant Voltage sources set to their values at Start Of Burn (SOB), that is at time of MD beginning;

- Case C: 17 MA plasma MD triggered by a Fast Discharge(FD); Induced currents are allowed in PF and CS coils simulated as stranded coils; FD begins closing  the PF and CS coils on the FD unit resistances assumed equal to 0.1 Ohm for all coils and setting to zero their power supply; the plasma MD is immediately triggered by the FD;

- Case D: Pure FD: FD in absence of plasma; Induced currents are allowed in PF and CS coils simulated as stranded coils; FD begins closing  the PFCs on a FD unit resistance assumed equal to 0.1 Ohm for all coils and setting to zero their power supply; No plasma current.

For all four cases the initial PF and CS coil currents are equal to their currents at SOB in the 17 MA plasma scenario (this is a conservative assumption for the case D); case C is the realistic simulation of PFC FD event as the plasma (whose current reduces the total) is, in any case, going to quench in case of fast discharge. Case D is, somehow conservative as the PF fast discharge without plasma is possible only before the start of discharge when the coil currents are considerably lower than at the start of burn. The resistances during FD have been rounded all 100 mOhm even though for an exact calculation they should start from the values indicated in table 5.1 and then increase during the discharge following the temperature increase in the FD units. It has been considered that as the temperature increase is not immediate the first part of the transient when the peaks occur won’t be substantially affected by the resistance change.

The model used for all cases was a 3D model of 20 degree normal ITER sector including, beside a coarse model of the in vessel components (blanket and divertor), a detailed model of the PF and CS coils, of the vessel and of the cryostat (figure 5.1). The Plasma disruption is the reference 17 MA DINA plasma disruption simulation (MD_UP_17MA_lin41ms) which is an upward major disruption with 41 ms linear current quench. The input for the 3-D FE analyses has been prepared using the EMAG code interface.

Table 5.1 - Table of Resistances of PFCs

| [mΩ] | CS3U | CS2U | CS1 |  | CS2L | CS3L |
| --- | --- | --- | --- | --- | --- | --- |
| Operational Resistance | 0.95 | 0.85 | 1.5 |  | 0.75 | 0.8 |
| FD Resistance | 110 | 122 | 134 |  | 122 | 98 |
|  | PF1 | PF2 | PF3 | PF4 | PF5 | PF6 |
| Operational Resistance | 0.8 | 0.7 | 1 | 0.95 | 1.1 | 0.7 |
| FD Resistance | 41 | 31 | 104 | 86 | 86 | 130 |

## Results of PFC-FD analysis

## Results of these analyses are summarised in figures 5.2 to 5.6, in particular:

- Figure 5.2: Total toroidal current vs. time during the event for the four cases. Total current is evaluated by B line integral along a closed poloidal path including plasma, vessel, in-vessel, PFCs and cryostat;

- Figure 5.3, 5.4, 5.5, 5.6: Field modulus time derivative (Bdot) vs. time for the cases A to D at equatorial plane and at distances of 16, 30, 60, 90 m respectively from tokamak axis.

The case A used as basis for the present document (and discussed in the previous sections 2 and 3) is confirmed to produce, with a safe margin, the worst foreseeable B_dot in the tokamak complex. The fast discharge of the poloidal field and central solenoid coils is demonstrated to produce lower B_dot than the plasma disruptions in both analysed cases: the realistic case of combined fast discharge and major disruption (case C) and in the more conservative assumption of pure magnets fast discharge in absence of plasma current (case D).

# Conclusions

Beside the study of section 5, a total of 12 cases have been analysed. The results of these analyses are summarized in the figures 3.1 to 3.12 and in the two tables below. In the tables, the maxima at equatorial level and at 17 m from tokamak axis (just outside the bio-shield) of the field components and of their times derivatives, are given for each case.

| 15 MA plasma (stray field at equatorial level just outside the bio-shield) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| case | Bx(mT) | Bz(mT) | ¦B¦(mT) | dBx/dt(mT/s) | dBz/dt(mT/s) | d¦B¦/dt(mT/s) |
| 1 | -17 | -144 | 145 | -6.7 | -32 | 33 |
| 2 | -16 | -143 | -144 | -6.8 | -31 | 31 |
| 3 | -39 | -119 | 121 | 4.8 | -5.5 | -5.5 |
| 4 | -39 | -119 | 121 | 4.7 | -5.2 | -5.2 |
| 5 | -38 | -162 | 164 | 4.1 | -5.6 | -5.6 |
| 6 | -38 | -162 | 164 | 4.05 | -5.6 | -5.6 |

| 17 MA plasma (stray field at equatorial level just outside the bio-shield) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| case | Bx(mT) | Bz(mT) | ¦B¦(mT) | dBx/dt(mT/s) | dBz/dt(mT/s) | d¦B¦/dt(mT/s) |
| 7 | -23 | -169 | 170 | -11.1 | -36.4 | 37.5 |
| 8 | -23 | 169 | 170.2 | -12.2 | -34.2 | 35.4 |
| 9 | -44 | -125 | 131 | 5 | -5.6 | -5.6 |
| 10 | -44 | -125 | 131 | 5 | -5.4 | -5.4 |
| 11 | -48 | -173 | 178 | 4.3 | -5.7 | -5.7 |
| 12 | -48 | -173 | 178 | 4.3 | -5.8 | -5.8 |

From these data it is apparent what follows:

- The stray field time derivatives are much higher during the plasma disruptions than during the normal operating scenarios and are slightly higher when the building concrete is conductor than when it is insulated;

- Due to the compensating effect of the plasma the maximum that the stray field achieves during a full scenarios without plasma is sensibly higher than the maximum in the correspondent scenarios that include the plasma;

- The maximum |B| reached during a full scenario is higher of than the maximum |B| reached after a plasma disruption starting from SOB of this scenario;

- During a normal operating scenario, due to the very slow time dependence of the currents in the plasma and in the PFC the stray field is in practice independent on the electrical properties of the conducting materials in the building.

As a consequence of these facts, for each plasma, at 15 and at 17 MA, only two of cases have been considered for the determination of the worst working conditions, due to the stray field, in the building region: 1) the disruption in presence of conducting building for the search of dBxdt, dBzdt and of d|B|/dt maxima; 2) the full scenario without plasma for the search of Bx, By and of |B| maxima.

The data of the mapping related to these cases are reported in the files quoted in section 3.1; Graphic maps reporting the field and field time derivative maxima level by level in the Tokamak Complex are available in [12].

# References

[1] M. Roccella R. Roccella -Assessment of Magnetic Field and its maximum time Derivative in Tokamak Building- ITER_D_ 3BQBVY v1.1

# [2] Magnetic Model of Tokamak Complex: MMTC1 ITER_D_283NY4 v1.7

# [3] DINA simulation of 15MA DT scenario: 2010-04c ITER_D_2PHQ3M

[4] Y.Gribov DINA_simulation_of_Representative_17MA_s_2LCQUN_v1_0- UID:2KTYCQ  -   2008

[5] R. Roccella guidelines for blanket load analysis UID:2LQQAG     30 May 2010

[6] VDE_DW_lin36ms (ITER_D_2ZTVMZ)

[7] MD_UP_17MA_lin41ms (ITER_D_A7GKXB)

# [8] LT08_FUS_028_ITER_Cryostat_Report_24_November_2009_rev_4 ITER/CT/07/381- Final report

# [9] 620000-CCS-Q00-05 DDD Outline Drawings for 62-11 62-14 62-19 62-74 Tokamak Complex Buildings - Structural ITER_D_34CKG9 v1.1

# [10] C. Neumeyer, Interaction of Tokamak Building Structures with ITER Magnetic Field (ITER_D_2FGN9P)

# [11] Preliminary Safety Report (RPrS) ITER_D_3ZR2NC v3.0

# [12] STATIC AND TRANSIENT MAGNETIC FIELD MAPS IN TOKAMAK BUILDING (ITER_D_QCTTFX)

# Figures

Fig 2.1 – Full operating scenario at 15 MA. The SOB occurs 75 s after the SOD. The plasma disruptions are assumed to occur at this of the scenario.

Fig 2.2 – Full operating scenario at 15 MA. Currents in the coils of CS.

Fig. 2.3– Full operating scenario at 15 MA. Current vs. time in the external poloidal coils

Fig. 2.4 - VDE_FD_III 36msLin CQ_15MA. Current in the central solenoid during the VDE the currents at t=0 correspond to the CS currents at t=75 s of fig 2.2.

Fig. 2.5 - VDE_FD_III 36msLin CQ_15MA. Current in the external poloidal coils during the VDE. The currents at t=0 correspond to the coils currents at t=75 s of fig 2.3.

Fig. 2.6 VDE_FD_III 36msLin CQ_15MA. Plasma current and position vs. time during the VDE. The currents at t=0 correspond to the coils currents at t=75 s of fig 2.3.

Fig 2.7 – Full operating scenario at 17 MA. Currents in the coils of CS.

Fig. 2.8– Full operating scenario at 17 MA. Current vs. time in the external poloidal coils

Fig 2.9 – Full operating scenario at 17 MA. The SOB occurs 152 s after the SOD. The plasma disruptions are assumed to occur at this of the scenario.

Fig. 2.10 – MD_ 41msLin CQ_17MA. Current in the central solenoid during the MD the currents at t=0 correspond to the CS currents at t=152 s of fig 2.7.

Fig. 2.11 - MD_ 41msLin CQ_17MA. Current in the external poloidal coils during the MD. The currents at t=0 correspond to the coils currents at t=152 s of fig 2.8.

Fig. 2.12 MD_ 41msLin CQ_17MA. Plasma current and position vs. time during the MD. The currents at t=0 correspond to the coils currents at t=152 s after the SOD.

Fig. 2.13 Building complex. Horizontal cross section at level 3 near the plasma level. Only the part of building included in the rectangle in magenta has been modelled.

| Fig.2.14 Building complex. Vertical cross section at section A-A of fig. 2.13. |
| --- |
| Fig 2.15 The conducting parts of the FEM. Beyond the Vessel and cryostat only the concrete up to 60 m. of radial distance and up to 18 m of height has been considered as conducting. Except of tokamak roof the conductivity the roof at this level has been neglected. |  |
| Fig. 2.16 – Particular of the model used in the analyses including the vessel the cryostat and the excitations (in blue). The plasma field and movement inside the vessel is reproduced with very good precision by the currents in the secondary excitations.. |
| Fig. 2.17 - The axis symmetric model used for the stray field evaluation inside the bioshield. In this case the effect of building has been neglected. |  |  |

Fig. 2.18 .The region including the building where the field map has been performed. In red is shown the region that has been mapped in the previos work on the same subject[1].

Fig 3.1 VDE_FD_III 36 ms lin CQ 15 MA. Case 1: Conducting building walls. Stray field (at left) and time derivative (at right) behaviour vs. time at the equatorial level and at various distances from tokamak axis..

Fig 3.2 VDE_FD_III 36 ms lin CQ 15 MA. Case 2: Non conducting building walls. Stray field (at left) and stray field time derivative (at right) behaviour vs. time at the equatorial level and at various distances from tokamak axis.

Fig 3.3 Full scenario at 15 MA. Case 3: Conducting building walls (including plasma). Stray field (at left) and stray field time derivative (at right) behaviour vs. time at the equatorial level and at various distances from tokamak axis.

Fig 3.4 Full scenario at 15 MA. Case 4: Non conducting building walls (including plasma). Stray field (at left) and stray field time derivative (at right) behaviour vs. time at the equatorial level and at various distances from tokamak axis.

Fig 3.5 Full scenario at 15 MA. Case 5: Conducting building walls (excluding plasma). Stray field (at left) and stray field time derivative (at right) behaviour vs. time at the equatorial level and at various distances from tokamak axis.

Fig 3.6 Full scenario at 15 MA. Case 6: Non conducting building walls (excluding plasma). Stray field (at left) and stray field time derivative (at right) behaviour vs. time at the equatorial level and at various distances from tokamak axis.

Fig 3.7 MD_ 41 ms lin CQ 17 MA. Case 7: Conducting building walls. Stray field (at left) and time derivative (at right) behaviour vs. time at the equatorial level and at various distances from tokamak axis.

Fig 3.8 MD_ 41 ms lin CQ 17 MA. Case 8: Non conducting building walls. Stray field (at left) and time derivative (at right) behaviour vs. time at the equatorial level and at various distances from tokamak axis.

Fig 3.9 Full scenario at 17 MA. Case 9: Conducting building walls (including plasma). Stray field (at left) and stray field time derivative (at right) behaviour vs. time at the equatorial level and at various distances from tokamak axis.

Fig 3.9 Full scenario at 17 MA. Case 10: Non conducting building walls (including plasma). Stray field (at left) and stray field time derivative (at right) behaviour vs. time at the equatorial level and at various distances from tokamak axis.

Fig 3.11 Full scenario at 17 MA. Case 11: Conducting building walls (excluding plasma). Stray field (at left) and stray field time derivative (at right) behaviour vs. time at the equatorial level and at various distances from tokamak axis.

Fig 3.12 Full scenario at 17 MA. Case 12: Non conducting building walls (excluding plasma). Stray field (at left) and stray field time derivative (at right) behaviour vs. time at the equatorial level and at various distances from tokamak axis.

| Fig.3.13 FDVDE36msLIN: Map of dBy/dt inside the bioshield. The map at right is on expanded scale with non uniform contour levels |  |
| --- | --- |
| Fig.3.14 - FDVDE36msLIN: Map of dBx/dt inside the bioshield. The map at right is on expanded scale with non uniform contour levels |  |

| Fig.3.15 - FDVDE36msLIN: Map of Bx inside the bioshield. The map at right is on expanded scale with non uniform contour levels |  |
| --- | --- |
| Fig.3.16 - FDVDE36msLIN: Map By inside the bioshield. The map at right is on expanded scale with non uniform contour levels |  |

| Fig.3.17 - MD16msEXP: Map dBy/dt inside the bioshield. The map at right is on expanded scale with non uniform contour levels |  |  |
| --- | --- | --- |
| Fig.3.18 - MD16msEXP: Map dBx/dt inside the bioshield. The map at right is on expanded scale with non uniform contour levels |  |  |
| Fig.3.19 - MD16msEXP: Map Bx inside the bioshield. The map at right is on expanded scale with non uniform contour levels |  |  |
| Fig.3.20 - MD16msEXP: Map By inside the bioshield. The map at right is on expanded scale with non uniform contour levels |  |  |

| Fig.3.21 - FUVDE36msLIN: Map dBy/dt inside the bioshield. The map at right is on expanded scale with non uniform contour levels |  |
| --- | --- |

| Fig.3.22 FUVDE36msLIN: Map dBx/dt inside the bioshield. The map at right is on expanded scale with non uniform contour levels |  |
| --- | --- |

| Fig.3.23 - FUVDE36msLIN: Map Bx inside the bioshield. The map at right is on expanded scale with non uniform contour levels |  |
| --- | --- |

| Fig.3.24 - FUVDE36msLIN: Map Bx inside the bioshield. The map at right is on expanded scale with non uniform contour level |  |
| --- | --- |

Fig. 3.25 a,b,c - Radial component of toroidal field on equatorial plane. In purple the section of TFC inboard and outboard legs. Dashed lines are:1inner VVl, 2 outer VV shell and 3 Cryostat.

3 2 1

a. Full scale: -4.38 to 4.38 T (r1= 8.8 m; r2 = 9.5; r3= 14 m)

b. Between -0.5 and 0.5 T

c. Between -0.05 and 0.05 T

Fig. 3.25 d,e - Radial component of toroidal field on equatorial plane. In purple the section of TFC inboard and outboard legs. Dashed lines are: inner VV shell, outer VV shell and Cryostat.

3 2 1

d. Between -0.006 and 0.006 T

e. Between -0.6∙10-3 and 0.6∙10-3 T

Fig. 3.26 a,b,c - Toroidal component of field on equatorial plane. In purple the section of TFC inboard and outboard legs. Dashed lines are: inner VV shell, outer VV shell and Cryostat.

3 2 1

a. Full scale: -11.6 to 3 T (r1= 8.8 m; r2 = 9.5; r3= 14 m)

b. Between -5 and -0.5 T

c. Between -0.5 and 3 T

Fig. 3.26 d,e,f - Toroidal component of field on equatorial plane. In purple the section of TFC inboard and outboard legs. Dashed lines are: inner VV shell, outer VV shell and Cryostat.

3 2 1

d. Between -0.17 and 0.22 T (r1= 8.8 m; r2 = 9.5; r3= 14 m)

e. Between -0.03 and 0.006 T

f. Between -0.003 and 0.001 T

Fig. 3.27 a,b,c – Toroida field modulus on equatorial plane. In purple the section of TFC inboard and outboard legs. Dashed lines are: 1 inner VV shell, 2 outer VV shell and 3 Cryostat.

1 2 3

a. Full scale: maximum = 11.6 T (r1= 8.8 m; r2 = 9.5; r3= 14 m)

c. Up to 5 T

c. Up to 0.5 T

Fig. 3.27 d,e,f – Toroida field modulus on equatorial plane. In purple the section of TFC inboard and outboard legs. Dashed lines are: 1 inner VV shell, 2 outer VV shell and 3 Cryostat.

3 2 1

d. Up to 0.06 T (r1= 8.8 m; r2 = 9.5; r3= 14 m)

e. Up to 0.006 T

f. Up to 0.8e-3 T

Fig 4.1 – Comparison of the poloidal stray field at level B1 in the Diagnostic Building (74) in the approved version 3.0 of the RPrS (left) and in the present updated document (right). Same , mirrored map apply to Tritium Building (14) as this is symmetric of the bld. 74 with respect to the PF/CS coil system.

Fig 4.2 – Comparison of the poloidal stray field at level B1 on the Assembly Hall side (Bld. 13) in the approved version 3.0 of the RPrS (top) and in the present updated document (bottom).

Fig 4.3 – Comparison of the poloidal stray field at level B1 on the Hot Cell side (Bld. 21) in the approved version 3.0 of the RPrS (top) and in the present updated document (bottom).

Fig 4.4 – Comparison of the 200, 50 and 10 mT zones between the RPrS document and the updated field maps: Blue dotted line: RPrS 200 mT zone; Yellow dotted line: RPrS 50 mT zone; Green dotted line: RPrS 10 mT zone; Blue dashed line: 200 mT updated; Yellow dashed line: 50 mT updated; Green dashed line: 10 mT updated.

Fig 4.5 – North-South section of the tokamak complex with maximum stray field (10-200 mT range). The 200 mT zone exceeds the bioshield concrete wall of about half meter at level L1-L2.

Figure 5.1 – conductive structures of thr Ansys 3D FE model used for the assessment of B_dot due to PF and CS fast discharge

Figure 5.2 - Total toroidal current (A) in the main conductive structures: Iplasma+Ipfc+Ivessel+Icryo versus time.

Figure 5.3 – Waveform of d¦B¦/dt vs. time in T/s for the four cases at the equatorial plane and at 16 m from tokamak axis.

Figure 5.4 – Waveform of d¦B¦/dt vs. time in T/s for the four cases at the equatorial plane and at 30 m from tokamak axis.

Figure 5.5 – Waveform of d¦B¦/dt vs. time in T/s for the four cases at the equatorial plane and at 60 m from tokamak axis.

Figure 5.6 – Waveform of d¦B¦/dt vs. time in T/s for the four cases at the equatorial plane and at 90 m from tokamak axis.